## Description of the agreement
Write function (mandatory)
Write Format
device address | function code | Register Starting Address |  | Number of write registers |  | Number of bytes written | write data |  |  |  |  | CRC check digit
1 byte | 1 byte | high byte (computing) | low byte | high byte (computing) | low byte | 1 byte | High Byte 1 | Low Byte 1 | … | High byte n | Low byte n | low byte | high byte (computing)
Broadcast address: 0x00; Device address: 1-247. | Write function code: 0x10 | [5 empty] | For 32-bit and 64-bit registers if there is no special instructions, the big-end mode is used to send. For example, 32-bit data is sent in the order of: byte3,byte2,byte1,byte0 |  |  |  |  | Modbus-CRC16 calculation is used.
Write Response Format
device address | function code | Register Starting Address |  | Number of write registers |  | CRC check digit
1 byte | 1 byte | high byte (computing) | low byte | high byte (computing) | low byte | low byte | high byte (computing)
local address | Write function code: 0x10 |  |  |  |  | Modbus-CRC16 calculation is used.
Read function (mandatory)
Read Format
device address | function code | Register Starting Address |  | Number of registers read |  | CRC check digit
1 byte | 1 byte | high byte (computing) | low byte | high byte (computing) | low byte | low byte | high byte (computing)
Equipment address: 1-247. | Read function code: 0x03 |  |  |  |  | Modbus-CRC16 calculation is used.
Retrieve answer format
device address | function code | Number of data bytes | Answer register data |  |  |  |  | CRC check digit
1 byte | 1 byte | 1 byte | High Byte 1 | Low Byte 1 | … | High byte n | Low byte n | low byte | high byte (computing)
local address | Read function code: 0x03 |  | For 32-bit and 64-bit registers if there is no special instructions, the big-end mode is used to send. For example, 32-bit data is sent in the order of: byte3,byte2,byte1,byte0 |  |  |  |  | Modbus-CRC16 calculation is used.
Individual write function (mandatory)
Individual Write Format
device address | function code | register address |  | register data |  | CRC check digit
1 byte | 1 byte | high byte (computing) | low byte | high byte (computing) | low byte | low byte | high byte (computing)
Equipment address: 1-247. | Single write function code: 0x06 |  |  |  |  | Modbus-CRC16 calculation is used.
Individual write response format
device address | function code | register address |  | register data |  | CRC check digit
1 byte | 1 byte | high byte (computing) | low byte | high byte (computing) | low byte | low byte | high byte (computing)
Equipment address: 1-247. | Single write function code: 0x06 |  |  |  |  | Modbus-CRC16 calculation is used.
Exception answering (mandatory)
device address | function code | error code |  | CRC check digit
1 byte | 1 byte | 1 byte |  | low byte | high byte (computing)
local address | Exception Function Code: 0x90 | See error code description |  | Modbus-CRC16 calculation is used.
error code |  |  | data encoding
(be) worth | clarification |  | Register Type |  | (be) worth |  | Send order (split into bytes to be transmitted from the left)
1 | illicit function |  | U16/S16 |  | 0x1234 |  | 0x12, 0x34
2 | illicit data address (computing) |  | U32/S32 |  | 0x12345678 |  | 0x56, 0x78, 0x12, 0x34
3 | illegal data value |  | UTF-8 string |  | ABCD |  | A, B, C, D
4 | From equipment failure
7 | Busy from equipment
Read and Write Properties
(be) worth | full name | clarification
R | Readable | readable register
W | Writable | Writable registers
V | volatile | Variable registers, support for frequent write operations, the number of writes is generally more than a million times
Preparation of the note
name (of a thing) | clarification
English name/field | The format is unified for the first letter of the combination of capital letters; word abbreviation is also the first letter of capital letters, other lowercase; the whole for the abbreviation of all capitals, proprietary vocabulary all capitals, do not allow all capitals of the two words together, can be in the middle of the preposition to connect.
Abbreviations
name (of a thing) | clarification
OVP | Over Voltage Protection
UVP | Under Voltage Protection
OFP | Over Frequency Protection
UFP | Under Frequency Protection
GFCI | Ground Fault Circuit Interrupter
OVRT | Over Voltage Ride-Through Error
LVRT | Low Voltage Ride-Through Error
AD | Analog-to-Digital
AC | Alternating Current
DC | Direct Current
MPPT | Maximum Power Point Tracking
SW | Software
HW | Hardware
RMS | Root Mean Square
OCP | Over current protection
LLC | Resonant Converters
DCI | Direct Current Injection
SN | Serial Number
SPD | Surge Protection Device
ID | Identification
PV | Photovoltaic
EPS | Emergency Power Supply
ISO | Insulation
PE | protecting earthing
SC | Short Circuit
BMS | Battery Management System
IGBT | Insulated GateBipolar Transistor
ZVP | Zero Voltage Protection
CAN | Controller Area Network
BCU | Battery Controller Unit
BMU | Battery Management Unit
PCC | Point of Common Coupling
CLS | Customer Export or Import Limitation Schemes
Rev | Reversal
Gen | Generator

## Address Description
| register address | field |  | typology | accurate | unit (of measure) | minimum value | maximum values | Read and Write Properties | clarification | classified classification | mask calculation |  | Supports single register reads | Supports single-register writes | Supports register concatenation | Supports register concatenation | note | Affiliated Projects
I. General (0x0040-0x00BF) |  |  | Address mask area description, this protocol version number, chip designator, inter-chip protocol version number, customer ID, etc.
Mask Area This 64 consecutive addresses | 0040 | AddressMask_General1 |  | U64 |  |  |  |  | R | The mask area of the 64 register address words beginning with this address. Each bit in this field corresponds to the validity of the 64 addresses in this field (each bit corresponds to a register address, including this field address). The corresponding bit is 0 for invalid and 1 for valid. Example: 0x0000 0x0000 0x0000 0x001F indicates that the 0x0044 address function is valid, the meaning of the mask area behind is the same, and the address interval to do the merge processing, not a single list. | end user | 0 | 0000000F |  |  | Start Address Length | Start Address Length | 16 address validity from address 0x0040 to address 0x004F
| 0041 | [9 empty] | end user | [6 empty] | 16 address validity from address 0x0050 to address 0x005F
| 0042 | [9 empty] | end user | [6 empty] | 16 address validity from address 0x0060 to address 0x006F
| 0043 | [9 empty] | end user | [6 empty] | 16 address validity from address 0x0070 to address 0x007F
Version number of this Agreement | 0044 | Modbus_Protocol_Version |  | BCD16 |  |  | 1.07 | 99.99 | R | Version Number of this Agreement. The Agreement version number corresponds to the version number on the cover page of this Agreement. | end user | [6 empty] | Note: Modbus protocol version number (BCD code) Bits 0-7 indicate the minor version number, where bits 0-3 indicate the low version number and bits 4-7 indicate the high version number. Bits 8-15 indicate the major version number, where bits 8-11 indicate the low version number and bits 12-15 indicate the high version number. Example: The value 0x1234 indicates that the protocol version number is 12.34
Chip Code (not available to the public) | 0045 | COMM_MCU_Code |  | ASCII |  |  |  |  | R | Communication chip designator. | end user | [6 empty] | Reference chip code specification, not open to the public. Need to convert ASCII code to corresponding characters. Example: Address 0x0045 is read as 0x4730 for "G0".
| 0046 | CTRL1_MCU_Code |  | ASCII |  |  |  |  | R | No. 1 control chip designator. | end user
| 0047 | CTRL2_MCU_Code |  | ASCII |  |  |  |  | R | Control chip designator #2. | end user
| 0048 -- 0051 | MCU_Code_Rsvd1 -- 10 | [7 empty] | MCU code reserved addresses 1-10 (10)
Internal Communication Protocol version number | 0052 | Protocol_ARM-DSPM |  |  |  |  | 0 | 0xFFFF | R | Protocol version number between ARM and DSPM. The high 8 bits correspond to the ARM-DSPM protocol version number. The low 8 bits correspond to the DSPM-ARM protocol version number. | end user | [6 empty] | The protocol version number needs to be the same for the inverter to work properly Check whether this function is used according to the model Example 1: 0x0102 means the protocol version number of ARM-DSPM is 001, and the protocol version number of DSPM-ARM is 002. Example 2: 0x0203 means the protocol version number of ARM-DSPS is 002, and the protocol version number of DSPS-ARM is 003. Example 3: 0x0304 means the protocol version number of DSPM-DSPS is 003 and the protocol version number of DSPS-DSPM is 004.
| 0053 | Protocol_ARM-DSPS |  |  |  |  | 0 | 0xFFFF | R | Protocol version number between ARM and DSPS. The high 8 bits correspond to the ARM-DSPS protocol version number, the The low 8 bits correspond to the DSPS-ARM protocol version number. | end user
| 0054 | Protocol_DSPM-DSPS |  |  |  |  | 0 | 0xFFFF | R | Protocol version number between DSPM and DSPS. The high 8 bits correspond to the DSPM-DSPS protocol version number. The low 8 bits correspond to the DSPS-DSPM protocol version number. | end user
| 0055 -- 0065 | Protocol_Version_Rsvd4 -- 20 | [7 empty] | Protocol version reserved addresses 4-20 (17)
| 0066 -- 007D | [8 empty] | reserve
Customer ID | 007E -- 0007F | Client ID_0 -- 1 | [6 empty] | RW | Distinguish between IDs 0-1 used by different customers. Refer to the customer coding specification Customer ID_0: used to mark customer ID, such as the default first flight is 0x0000. Customer ID_1: Alternate Expansion | end user | [6 empty] | Example: Trina 0x0001, Skyworth 0x0002, etc.
| 0080 -- 00083 | [8 empty] | reserve
CPLD version number | 0084 | CPLDVersion0 |  | ASCII |  |  |  |  | R | Master controller chip software version number stage definition bits. The lower 8 bits of the register hold the ASCII code. The default value for the official version is 'V'. Register high 8 bits hold the high digit; Register low 8 bits hold the low digit.
| 0085 | CPLDVersion1 |  | ASCII |  |  |  |  | R | Master controller chip software master version number. All chip master version numbers in the same system must be the same, otherwise it is considered a system failure. The high 8 bits of the register store the high digit; The lower 8 bits of the register store the lower digit.
| 0086 | CPLDVersion2 |  | ASCII | [5 empty] | Non-standard customized version number of the main controller chip software. The version number of the standard software is "00". The non-standard customized version number of all chips in the same system must be the same, otherwise it is regarded as a system failure. The high 8 bits of the register store the high digits; The lower 8 bits of the register store the lower digits.
| 0087 | CPLDVersion3 |  | ASCII | [5 empty] | Host controller chip software subversion number. The high 8 bits of the register hold the high digit; The low 8 bits of the register hold the low digit.
Equipment code | 0088 | ProjectNum |  | U16 * 1 |  |  |  | R | R | Project designator to distinguish the region's data definitions, enumeration type: 0: 225KTLX-HV project; 1: CBS5000 project; Other - Reserved
Equipment Reservation | 0089 -- 0008B | Reserved |  | U16 * 3 |  |  |  | RW | RW | Reserved, readout is 0
II. Real-time data area (0x0400-0x07FF) | [19 empty] | Total number of registers
2.1 System Information (0x0400-0x047F) |  |  | Operational status, fault information table, grid connection waiting time, temperature values, system and generation time, machine serial number, status information, software version information, etc. | [16 empty] | 181
| 0400 -- 0403 | AddressMask_Realtime_SysInfo1 |  | U64 |  |  |  |  | R | Mask area for the 64 register address words starting at this address. Refer to the description of address 0x0040 | end user | 0 | 0000000F
operational state | 0404 | SysState |  | U16 |  |  |  |  | R | Running status. 0: Waiting status 1: Detection status 2: Grid-connected status 3: Emergency power supply state 4: Recoverable fault state 5: Permanent fault state 6: Upgrade status 7：Self-charging state 8：SVG state 9：PID state 10：Load limit status | end user | [6 empty] | The operating state of the inverter, 3, 6-9 of the state to distinguish between models Example: 0x0004 means the inverter is in recoverable fault state
Fault Information Sheet 2-1 | 0405 -- 0416 | Fault1 - 18 |  | U16 |  |  |  |  | R | Fault Information Tables 1-18 (18). Record inverter fault messages, and also extended 19-30 addresses at 0x0432-043D | end user | [6 empty] | For the corresponding fault information, see the other worksheet of this table "Fault Location Description". Example: A value of 0x0002 read from 0x0405 indicates that the inverter has a grid undervoltage fault.
Waiting time for grid connection | 0417 | Countdown |  | U16 | 1 | unit of angle or arc equivalent one sixtieth of a degree |  |  | R | Grid-connection waiting time (power-on countdown) | end user | [6 empty] | Grid-connected wait time, boot-up countdown available for viewing Example: 0x003C means the power-up time is 60 seconds
temp | 0418 -- 0419 | Temperature_Env1 -- 2 |  | I16 | 1 | ℃ |  |  | R | Ambient temperature 1-2 (2) | end user | [6 empty] | Example: 0x0001 means the ambient temperature 1 is 1°C
| 041A -- 041F | Temperature_HeatSink1 -- 6 |  | I16 | 1 | ℃ |  |  | R | Radiator temperature 1-6 (6) | end user | [6 empty] | Whether this function is available or not depends on the model, you can check whether the corresponding registers are used according to the mask. For example, please refer to 0x0418 address description
| 0420 -- 0422 | Temperature_Inv1 -- 3 |  | I16 | 1 | ℃ |  |  | R | Module temperature 1-3 (3) | end user
| 0423 -- 0425 | Temp_Rsvd1 -- 3 |  | I16 | 1 | ℃ |  |  | R | Reserved temperature 1-3 (3) | end user
Power generation, running time | 0426 | GenerationTime_Today |  | U16 | 1 | minutes |  |  | R | Power generation time of the day | end user | [6 empty] | Today's power generation time of the inverter, start timing after grid connection Example: 0x0001 means 1 minute of power generation for the day.
| 0427 -- 0428 | GenerationTime_Total |  | U32 | 1 | minutes |  |  | R | Total power generation time | end user | [6 empty] | Timing starts after the inverter is connected to the grid and occupies two registers, example: 0x0000 0x087E means the total power generation time is 2174 minutes
| 0429 -- 042A | ServiceTime_Total |  | U32 | 1 | minutes |  |  | R | Total Running Time | end user | [6 empty] | Inverter power-up start timing, occupies two registers, example: 0x0000 0x09C5 refers to the total running time of 2501 minutes
Insulation impedance | 042B | InsulationResistance |  | U16 | 1 | kΩ |  |  | R | Insulation impedance | end user | [6 empty] | Insulation impedance magnitude, detected by the inverter in the detection state
System Time 2-1 | 042C | SysTime_Year |  | U16 |  |  |  |  | R | System time - years | end user | [6 empty] | The actual year is in 2000 plus the readout Example: 0x0016 means 2022
| 042D | SysTime_Month |  | U16 |  |  |  |  | R | System time-months | end user | [6 empty] | Example: 0x0005 means May
| 042E | SysTime_Date |  | U16 |  |  |  |  | R | System time - day | end user | [6 empty] | Example: 0x000F means 15 days
| 042F | SysTime_Hour |  | U16 |  |  |  |  | R | System time - hour | end user | [6 empty] | Example: 0x0010 means 16 hours
| 0430 | SysTime_Minute |  | U16 |  |  |  |  | R | System time - minutes | end user | [6 empty] | Example: 0x0020 means 32 points
| 0431 | SysTime_Second |  | U16 |  |  |  |  | R | System Time-Second | end user | [6 empty] | Example: 0x0030 means 48 seconds
Fault Information Sheet 2-2 | 0432 -- 043D | Fault 19 - 30 |  | U16 |  |  |  |  | R | Fault Message Tables 19-30 (12). Record inverter fault messages, first 18 at address 0x0418 | end user | [6 empty] | Corresponding to the fault information to see this form of another worksheet "fault bit field description", the case please see the 0x0405 address notes
Fan speed | 043E | SpeedFan |  | U16 |  | r/min |  |  | R | Fan speed | end user
| 043F | [7 empty] | R | reserve | [7 empty] | Is there a conflict with the definition of address 0x1070?
| 0440 -- 0443 | AddressMask_Realtime_SysInfo2 |  | U64 |  |  |  |  | R | Mask area for the 64 register address words starting at this address. Refer to the description of address 0x0040 | end user | 0 | 0000000F
| 0444 | Production_Code |  | U16 | [5 empty] | reserve
Machine Serial Number 2-1 | 0445 -- 044C | Serial_Number0 -- 7 |  | ASCII |  |  |  |  | R | Machine serial number Serial_Number0-7 (8, indicating serial number bits 1-16), bits 17-20 are at register addresses 0x0470 and 0x0471 | end user | [6 empty] | To parse, you need to check DCC's barcode rule definition document. Serial_Number0 is serial number bits 1 and 2, and so on. The high 8 bits of the register store the 1st bit of the serial number; The lower 8 bits of the register store the second bit of the serial number. Example: 0x5353 means "SS".
Hardware version number | 044D -- 044E | Hardware_Version0 -- 1 |  | ASCII |  |  |  |  | R | Hardware version number 0-2 (2, 4 ASCII bits) | end user | [6 empty] | Address 0x044D indicates bits 1 and 2. And so on. The high 8 bits of the register hold bit 1 of the sequence number; The lower 8 bits of the register hold bit 2 of the sequence number. Example: 0x5630 refers to "V0", 0x3033 refers to "03", actual measurement: V003
Communication Chip Software version number | 044F | Software_Version_Stage_COM |  | ASCII |  |  |  |  | R | Communication chip software version number stage definition bits. The lower 8 bits of the register hold the ASCII code. The default value for the official version is 'V'. | end user | [6 empty] | Address 0x044F has 'V', 'G', 'I' and other versions, are the official version of the 0G100003 means that the software version number of the communication chip is G100003. Example 1: Address 0x044F reads 0x3047, which means "0G". Example 2: Address 0x0450 read 0x3130 means "10". Example 3: 0x3030 read from address 0x0451 means "00".
| 0450 | Software_Version_Major_COM |  | ASCII |  |  |  |  | R | Communication chip software master version number. All chip master version numbers in the same system must be the same, otherwise it is regarded as a system failure. The high 8 bits of the register store the high digit; The lower 8 bits of the register store the lower digit. | end user
| 0451 | Software_Version_Custom_COM |  | ASCII |  |  |  |  | R | Non-standard customized version number of communication chip software. The version number of the standard software is "00". The non-standard customized version number of all chips in the same system must be the same, otherwise it is regarded as a system failure. The high 8 bits of the register store the high digit; The lower 8 bits of the register store the lower digits. | end user
| 0452 | Software_Version_Minor_COM |  | ASCII |  |  |  |  | R | Communication chip software subversion number. The high 8 bits of the register store the high digit; The lower 8 bits of the register hold the lower digit. Example: 0x3033 means "03". | end user
Main Controller Chip Software version number | 0453 | Software_Version_Stage_Master |  | ASCII |  |  |  |  | R | Master controller chip software version number stage definition bits. The lower 8 bits of the register hold the ASCII code. The default value for the official version is 'V'. Register high 8 bits hold the high digit; Register low 8 bits hold the low digit. | end user | [6 empty] | Address 0x0453 may have other characters For case study, please check the description of the software version number of the communication chip. 0V100002 means that the software version number of the main controller chip is V100002.
| 0454 | Software_Version_Major_Master |  | ASCII |  |  |  |  | R | Master controller chip software master version number. All chip master version numbers in the same system must be the same, otherwise it is considered a system failure. The high 8 bits of the register store the high digit; The lower 8 bits of the register store the lower digit. | end user
| 0455 | Software_Version_Custom_Master |  | ASCII |  |  |  |  | R | Non-standard customized version number of the main controller chip software. The version number of the standard software is "00". The non-standard customized version number of all chips in the same system must be the same, otherwise it is regarded as a system failure. The high 8 bits of the register store the high digits; The lower 8 bits of the register store the lower digits. | end user
| 0456 | Software_Version_Minor_Master |  | ASCII |  |  |  |  | R | Host controller chip software subversion number. The high 8 bits of the register hold the high digit; The low 8 bits of the register hold the low digit. | end user
Sub-Controller Chip Software version number | 0457 | Software_Version_Stage_Slave |  | ASCII |  |  |  |  | R | Subcontroller chip software version number stage definition bits. The lower 8 bits of the register hold the ASCII code. The default value for the official version is 'V'. Register high 8 bits hold the high digit; Register low 8 bits hold the low digit. | end user | [6 empty] | Address 0x0457 may have other characters For case study, please check the description of the software version number of the communication chip. 0L100000 means that the software version number of the sub controller chip is L100000.
| 0458 | Software_Version_Major_Slave |  | ASCII |  |  |  |  | R | Sub controller chip software master version number. All chip master version numbers in the same system must be the same, otherwise it is considered a system failure. The high 8 bits of the register store the high digit; The low 8 bits of the register store the low digit. | end user
| 0459 | Software_Version_Custom_Slave |  | ASCII |  |  |  |  | R | Non-standard customized version number of the sub-controller chip software. The version number of the standard software is "00". The non-standard customized version number of all chips in the same system must be the same, otherwise it is regarded as a system failure. The high 8 bits of the register store the high digits; The lower 8 bits of the register store the lower digits. | end user
| 045A | Software_Version_Minor_Slave |  | ASCII |  |  |  |  | R | Subcontroller chip software subversion number. The high 8 bits of the register hold the high digit; The low 8 bits of the register hold the low digit. | end user
Safety Regulations Library version number | 045B | Safety_Version_Major |  | ASCII |  |  |  |  | R | Safety library master version number Example: 0x3036 means 06 master version | end user
| 045C | Safety_version_Minor |  | ASCII |  |  |  |  | R | Safety library sub-version number Example: 0x3038 refers to sub-version 08 | end user
BOOT version number | 045D | Boot_Version_COM |  | U16 |  |  |  |  | R | BOOT version number of the communication board | end user
| 045E | Boot_Version_Master |  | U16 |  |  |  |  | R | BOOT version number of the main DSP | end user
| 045F | Boot_Version_Slave |  | U16 |  |  |  |  | R | BOOT version number of the secondary DSP | end user
Safety Certification Relevant version number | 0460 | Safety_Firmware_Version_Stage |  | ASCII |  |  |  |  | R | Safety Certification Software Version Number Phase Definition Bits. The lower 8 bits of the register hold the ASCII code. The default value for the official version is 'V'. Register high 8 bits hold the high digit; Register low 8 bits hold the low digit. | end user | [6 empty] | Case study please check the communication chip software version number description 0V000001 means the version number of safety software certification is V000001.
| 0461 | Safety_Firmware_Version_Major |  | ASCII |  |  |  |  | R | Safety certification software master version number. All chip master version numbers in the same system must be the same, otherwise it is considered as a system failure. The high 8 bits of the register store the high digit; The low 8 bits of the register store the low digit. | end user
| 0462 | Safety_Firmware_Version_Custom |  | ASCII |  |  |  |  | R | Non-standard customized version number of safety certification software. The version number of the standard software is "00". The non-standard customized version number of all chips in the same system must be the same, otherwise it is regarded as a system failure. The high 8 bits of the register store the high digits; The lower 8 bits of the register store the lower digits. | end user
| 0463 | Safety_Firmware_Version_Minor |  | ASCII |  |  |  |  | R | Safety certification software subversion number. The high 8 bits of the register hold the high digit; The low 8 bits of the register hold the low digit. | end user
| 0464 | Safety_Hardware_Version0 |  | ASCII |  |  |  |  | R | Safety certification hardware version number bits 1 and 2. The high 8 bits of the register hold bit 1 of the serial number; The low 8 bits of the register hold bit 2 of the serial number. | end user | [6 empty] | Case study please check the hardware version number description Test: Safety hardware certification version number is V201
| 0465 | Safety_Hardware_Version1 |  | ASCII |  |  |  |  | R | Safety certification hardware version number bits 3 and 4. The high 8 bits of the register store the 3rd bit of the serial number; The low 8 bits of the register hold bit 4 of the serial number. | end user
AFCI version number | 0466 | Afci_Ver_Firmware |  | ASCII |  |  |  |  | R | afci firmware version number 'V'. The high 8 bits are reserved; Lower 8 bits hold the version number. | [7 empty] | For case study, please check the description of the software version number of the communication chip. Please check the ASCII translation
| 0467 | Afci_Ver_Sft |  | ASCII |  |  |  |  | R | afci software version. The high 8 bits hold bit 1; The low 8 bits store bit 2.
| 0468 | Afci_Ver_Hard |  | ASCII |  |  |  |  | R | afci hardware version The high 8 bits hold bit 1; The low 8 bits store bit 2.
| 0469 | Afci_Srs_Hard |  | ASCII |  |  |  |  | R | afci hardware serial number. The high 8 bits store bit 1; The low 8 bits store bit 2.
| 046A | Afci_Ver_Com |  | ASCII |  |  |  |  | R | afci communication version. The high 8 bits store bit 1; The low 8 bits store bit 2.
Safety Documentation Packages Version number | 046B | Safety_Package_Version0 |  | ASCII |  |  |  |  | R | Safety file package version number bits 1 and 2. The high 8 bits of the register hold bit 1 of the serial number; The low 8 bits of the register hold bit 2 of the serial number. | [7 empty] | For case study, please check the communication chip software version number description please check the translation against ASCII code.
| 046C | Safety_Package_Version1 |  | ASCII |  |  |  |  | R | Bits 3 and 4 of the version number of the safety file package. The high 8 bits of the register hold bit 3 of the serial number; The low 8 bits of the register hold bit 4 of the serial number.
| 046D -- 046F | [8 empty] | reserve
Machine Serial Number 2-2 | 0470 -- 0471 | Serial_Number8 -- 9 |  | ASCII |  |  |  |  | R | Machine serial number Serial_Number8-9. Indicates bits 17-20, bits 1-16 are in register address 0x0445 | end user | [6 empty] | Bits 15-20 of the sequence number are used in the 20-bit sequence number and are not used in the 14-bit sequence number Register 0x0470 high 8 bits holds bit 17 of the sequence number; Register 0x0470 low 8 bits holds the 18th bit of the sequence number.
| 0472 -- 0476 | Serial_Number11_Rsvd0 -- 4 |  | ASCII |  |  |  |  | R | Reserved 0-4 (5)
status message table | 0477 - 047F | State1 - 9 |  | U16 |  |  |  |  | R | Status Information Tables 1-9 (9). Record status information of the inverter | end user | [6 empty] | For the corresponding status information, see the other worksheet of this form, "Status Information Sheet".
2.2 Parallel output (0x0480-0x04FF) |  |  | Real-time acquisition data for grid-connected operation
| 0480 -- 0483 | AddressMask_Realtime_GridOutput1 |  | U64 |  |  |  |  | R | Mask area for the 64 register address words starting at this address. Refer to the description of address 0x0040 | end user | 0 | 0000000F
grid frequency | 0484 | Frequency_Grid |  | U16 | 0.01 | Hz |  |  | R | Grid Frequency. | end user | [6 empty] | Example: 0x138B means 50.03Hz
Power data | 0485 | ActivePower_Output_Total |  | I16 | 0.01 | kW |  |  | R | Total active power. | end user | [6 empty] | The output power of the inverter, discharging is positive, charging is negative Example: 0x006A means 1.06KW
| 0486 | ReactivePower_Output_Total |  | I16 | 0.01 | kW |  |  | R | Total reactive power. | end user | [6 empty] | The electrical power used to establish and maintain a magnetic field in a device, with positive overrun and negative lag at the inverter end
| 0487 | ApparentPower_Output_Total |  | I16 | 0.01 | kW |  |  | R | Total vision in power. | end user | [6 empty] | Maximum active power of the current voltage and current of the inverter, positive for discharging and negative for charging
| 0488 | ActivePower_PCC_Total |  | I16 | 0.01 | kW |  |  | R | Total PCC active power. | end user | [6 empty] | Energy flow chart grid power reading address, some models need to be connected to the meter to have data, sell power is positive, buy power is negative
| 0489 | ReactivePower_PCC_Total |  | I16 | 0.01 | kW |  |  | R | Total PCC reactive power. | end user | [6 empty] | Positive for overrun and negative for lag at inverter side
| 048A | ApparentPower_PCC_Total |  | I16 | 0.01 | kW |  |  | R | Total PCC apparent power. | end user | [6 empty] | Selling electricity is positive, buying electricity is negative
| 048B | ActivePower_PCC_Total2 |  | I16 | 0.1 | kW |  |  | R | Total PCC active power 2. 1. and 0488 address difference is different precision 2.0488 address data overflow, then use this address | end user
| 048C | GridOutput_Rsvd1 | [6 empty] | R | Grid-connected output reserved for 1 | end user
R-phase grid-connected Real-time data | 048D | Voltage_Phase_R |  | U16 | 0.1 | V |  |  | R | R-phase grid voltage | end user | [6 empty] | Example: 0x093E indicates 236.6V
| 048E | Current_Output_R |  | U16 | 0.01 | A |  |  | R | R-phase inverter output current | end user | [6 empty] | Example: 0x0049 means 0.73A
| 048F | ActivePower_Output_R |  | I16 | 0.01 | kW |  |  | R | The R-phase inverter outputs active power. | end user | [6 empty] | Discharge is positive, charge is negative
| 0490 | ReactivePower_Output_R |  | I16 | 0.01 | kW |  |  | R | The R-phase inverter outputs reactive power. | end user | [6 empty] | Positive for overrun and negative for lag at inverter side
| 0491 | PowerFactor_Output_R |  | I16 | 0.001 | p.u. |  |  | R | R-phase power factor. | end user | [6 empty] | Positive for overrun and negative for lag at inverter side
| 0492 | Current_PCC_R |  | U16 | 0.01 | A |  |  | R | R-phase PCC current. | end user | [6 empty] | Some models need to be connected to a power meter to get data
| 0493 | ActivePower_PCC_R |  | I16 | 0.01 | kW |  |  | R | R-phase PCC active power | end user | [6 empty] | Positive for overrun and negative for lag at inverter side
| 0494 | ReactivePower_PCC_R |  | I16 | 0.01 | kW |  |  | R | R-phase PCC reactive power. | end user
| 0495 | PowerFactor_PCC_R |  | I16 | 0.001 | p.u. |  |  | R | R-phase PCC power factor. | end user | [6 empty] | Positive for overrun and negative for lag at inverter side
| 0496 -- 0497 | R_Rsvd1 -- 2 | [6 empty] | R | R-phase reserved 1-2 | end user
S-phase grid-connected Real-time data | 0498 | Voltage_Phase_S |  | U16 | 0.1 | V |  |  | R | S-phase grid voltage | end user | [6 empty] | Refer to the relevant note on R-phase above
| 0499 | Current_Output_S |  | U16 | 0.01 | A |  |  | R | S-phase inverter output current | end user
| 049A | ActivePower_Output_S |  | I16 | 0.01 | kW |  |  | R | The S-phase inverter outputs active power. | end user
| 049B | ReactivePower_Output_S |  | I16 | 0.01 | kW |  |  | R | The S-phase inverter outputs reactive power. | end user
| 049C | PowerFactor_Output_S |  | I16 | 0.001 | p.u. |  |  | R | S-phase power factor. | end user
| 049D | Current_PCC_S |  | U16 | 0.01 | A |  |  | R | S-phase PCC current | end user
| 049E | ActivePower_PCC_S |  | I16 | 0.01 | kW |  |  | R | S-phase PCC active power. | end user
| 049F | ReactivePower_PCC_S |  | I16 | 0.01 | kW |  |  | R | S-phase PCC reactive power. | end user
| 04A0 | PowerFactor_PCC_S |  | I16 | 0.001 | p.u. |  |  | R | S-phase PCC power factor. | end user
| 04A1 -- 04A2 | S_Rsvd1 -- 2 | [6 empty] | R | S-phase reserved 1-2 | end user
T-phase grid connection Real-time data | 04A3 | Voltage_Phase_T |  | U16 | 0.1 | V |  |  | R | T-phase grid voltage | end user | [6 empty] | Refer to the relevant note on R-phase above
| 04A4 | Current_Output_T |  | U16 | 0.01 | A |  |  | R | T-phase inverter output current | end user
| 04A5 | ActivePower_Output_T |  | I16 | 0.01 | kW |  |  | R | The T-phase inverter outputs active power. | end user
| 04A6 | ReactivePower_Output_T |  | I16 | 0.01 | kW |  |  | R | The T-phase inverter outputs reactive power. | end user
| 04A7 | PowerFactor_Output_T |  | I16 | 0.001 | p.u. |  |  | R | T-phase power factor. | end user
| 04A8 | Current_PCC_T |  | U16 | 0.01 | A |  |  | R | T-phase PCC current. | end user
| 04A9 | ActivePower_PCC_T |  | I16 | 0.01 | kW |  |  | R | T-phase PCC active power. | end user
| 04AA | ReactivePower_PCC_T |  | I16 | 0.01 | kW |  |  | R | T-phase PCC reactive power. | end user
| 04AB | PowerFactor_PCC_T |  | I16 | 0.001 | p.u. |  |  | R | T-phase PCC power factor. | end user
| 04AC -- 04AD | T_Rsvd1 -- 2 | [6 empty] | R | T-phase reserved 1-2 | end user
Other Grid Integration Real-time data | 04AE | ActivePower_PV_Ext |  | U16 | 0.01 | kW |  |  | R | External power generation | end user | [6 empty] | The number read out multiplied by the precision is the final data.
| 04AF | ActivePower_Load_Sys |  | U16 | 0.01 | kW |  |  | R | Total system load power | end user | [6 empty] | Need to connect the load, can flow chart load power reading address
| 04B0 | Voltage_Phase_L1N |  | U16 | 0.1 | V |  |  | R | Grid L1 to N voltage rms | end user
| 04B1 | Current_Output_L1N |  | U16 | 0.01 | A |  |  | R | L1 Output Current RMS | end user
| 04B2 | ActivePower_Output_L1N |  | I16 | 0.01 | kW |  |  | R | Active power output on line L1 | end user
| 04B3 | Current_PCC_L1N |  | U16 | 0.01 | A |  |  | R | RMS CT current on L1 line | end user
| 04B4 | ActivePower_PCC_L1N |  | I16 | 0.01 | kW |  |  | R | PCC active power on line L1 | end user
| 04B5 | Voltage_Phase_L2N |  | U16 | 0.1 | V |  |  | R | Grid L2 to N voltage rms | end user
| 04B6 | Current_Output_L2N |  | U16 | 0.01 | A |  |  | R | L2 Output Current RMS | end user
| 04B7 | ActivePower_Output_L2N |  | I16 | 0.01 | kW |  |  | R | Active power output on line L2 | end user
| 04B8 | Current_PCC_L2N |  | U16 | 0.01 | A |  |  | R | RMS CT current on L2 line | end user
| 04B9 | ActivePower_PCC_L2N |  | I16 | 0.01 | kW |  |  | R | PCC active power on line L2 | end user
| 04BA | Voltage_Line_L1 |  | U16 | 0.1 | V |  |  | R | L1 line voltage: voltage between phases R/S | end user | [6 empty] | This function is only available for three-phase models, e.g. 0x1014 means 411.6V.
| 04BB | Voltage_Line_L2 |  | U16 | 0.1 | V |  |  | R | L2 line voltage: voltage between S/T phases | end user | [6 empty] | Reference L1 line voltage
| 04BC | Voltage_Line_L3 |  | U16 | 0.1 | V |  |  | R | L3 line voltage: voltage between phases T/R | end user
| 04BD | Power_Factor |  | I16 | 0.001 | p.u. |  |  | R | Total power factor. | end user | [6 empty] | Positive for overrun and negative for lag at inverter side
| 04BE | Current_HV_LLC_Chg_Dchg |  | I16 | 0.01 | A |  |  | R | HV side LLC charge/discharge current | end user
2.3 Off-grid output (0x0500-0x057F) |  |  | Real-time acquisition data for off-grid operation
| 0500 -- 0503 | AddressMask_Realtime_EmergencyOutput1 |  | U64 |  |  |  |  | R | Mask area for the 64 register address words starting at this address. Refer to the description of address 0x0040 | end user | 0 | 0000000F
load power | 0504 | ActivePower_Load_Total |  | I16 | 0.01 | kW |  |  | R | Load active power. | end user | [6 empty] | Load consumption is positive and feedback is negative.
| 0505 | ReactivePower_Load_Total |  | I16 | 0.01 | kW |  |  | R | Load reactive power | end user
| 0506 | ApparentPower_Load_Total |  | I16 | 0.01 | kW |  |  | R | Load apparent power. | end user | [6 empty] | Load consumption is positive and feedback is negative.
Output Voltage Frequency | 0507 | Frequency_Output |  | U16 | 0.01 | Hz |  |  | R | Output Voltage Frequency | end user | [6 empty] | Voltage frequency of the inverter output
| 0508 -- 0509 | ESOutput_Rsvd1 -- 2 | [6 empty] | R | Off-grid total output reserved 1-2 | end user
R phase off network Real-time data | 050A | Voltage_Output_R |  | U16 | 0.1 | V |  |  | R | R-phase inverter output voltage | end user
| 050B | Current_Load_R |  | I16 | 0.01 | A |  |  | R | R-phase load current | end user | [6 empty] | Current between phase R and the load
| 050C | ActivePower_Load_R |  | I16 | 0.01 | kW |  |  | R | R-phase load active power. | end user | [6 empty] | Single-phase loads have active power with positive load consumption and negative feedback.
| 050D | ReactivePower_Load_R |  | I16 | 0.01 | kW |  |  | R | R-phase load reactive power. | end user | [6 empty] | Positive for overrun and negative for lag at inverter side
| 050E | ApparentPower_Load_R |  | I16 | 0.01 | kVA |  |  | R | R-phase load apparent power. | end user | [6 empty] | Load consumption is positive and feedback is negative.
| 050F | LoadPeakRatio_R |  | U16 | 0.01 | p.u. |  |  | R | R-phase load peak ratio | end user
| 0510 | Voltage_Load_R |  | U16 | 0.1 | V |  |  | R | R Corresponding emergency load voltage | end user
| 0511 | ESR_Rsvd2 | [6 empty] | R | R-phase reserved 2 | end user
S-phase off-grid Real-time data | 0512 | Voltage_Output_S |  | U16 | 0.1 | V |  |  | R | S-phase inverter output voltage | end user | [6 empty] | Refer to the relevant note on R-phase above
| 0513 | Current_Load_S |  | I16 | 0.01 | A |  |  | R | S-phase load current | end user
| 0514 | ActivePower_Load_S |  | I16 | 0.01 | kW |  |  | R | S-phase load active power. | end user
| 0515 | ReactivePower_Load_S |  | I16 | 0.01 | kW |  |  | R | S-phase load reactive power. | end user
| 0516 | ApparentPower_Load_S |  | I16 | 0.01 | kVA |  |  | R | S-phase load apparent power. | end user
| 0517 | LoadPeakRatio_S |  | U16 | 0.01 | p.u. |  |  | R | S-phase load peak ratio | end user
| 0518 | Voltage_Load_S |  | U16 | 0.1 | V |  |  | R | S corresponding emergency load voltage | end user
| 0519 | ESS_Rsvd2 | [6 empty] | R | S-phase reserved 2 | end user
T-phase off-grid Real-time data | 051A | Voltage_Output_T |  | U16 | 0.1 | V |  |  | R | T-phase inverter output voltage | end user | [6 empty] | Refer to the relevant note on R-phase above
| 051B | Current_Load_T |  | I16 | 0.01 | A |  |  | R | T-phase load current | end user
| 051C | ActivePower_Load_T |  | I16 | 0.01 | kW |  |  | R | T-phase load active power. | end user
| 051D | ReactivePower_Load_T |  | I16 | 0.01 | kW |  |  | R | T-phase load reactive power. | end user
| 051E | ApparentPower_Load_T |  | I16 | 0.01 | kVA |  |  | R | T-phase load apparent power. | end user
| 051F | LoadPeakRatio_T |  | U16 | 0.01 | p.u. |  |  | R | T-phase load peak ratio | end user
| 0520 | Voltage_Load_T |  | U16 | 0.1 | V |  |  | R | T corresponding emergency load voltage | end user
| 0521 | EST_Rsvd2 | [6 empty] | R | T-phase reserved 2 | end user
Other off-grid Real-time data | 0522 | Voltage_Output_L1N |  | U16 | 0.1 | V |  |  | R | Inverter L1 to N voltage rms | end user
| 0523 | Current_Load_L1N |  | I16 | 0.01 | A |  |  | R | L1 Load current rms value | end user
| 0524 | ActivePower_Load_L1N |  | I16 | 0.01 | kW |  |  | R | Load L1 to N active power | end user
| 0525 | Voltage_Output_L2N |  | U16 | 0.1 | V |  |  | R | Inverter L2 to N voltage rms | end user
| 0526 | Current_Load_L2N |  | I16 | 0.01 | A |  |  | R | L2 load current rms | end user
| 0527 | ActivePower_Load_L2N |  | I16 | 0.01 | kW |  |  | R | Load L2 to N active power | end user
2.4PV input (0x0580-0x05FF) |  |  | 1st-16th PV voltage, current and power values and total PV power
| 0580 -- 0583 | AddressMask_Realtime_Input_PV1 |  | U64 |  |  |  |  | R | Mask area for the 64 register address words starting at this address. Refer to the description of address 0x0040 | end user | 0 | 0000000F
PV1-16 Voltage Current Wattage Data | 0584 -- 05B1 | Voltage_PV1 -- 16 |  | U16 | 0.1 | V |  |  | R | PV voltages for channels 1-16 (16). Addresses start at 0x0584 and are spaced 3 addresses apart each way. | end user | [6 empty] | The number of PV paths is related to the specific model. Read out the number multiplied by the precision is the final data Example 1: Address 0x0584 read: 0x0906 for 231V Example 2: Address 0x0585 read: 0x01BB for 4.43A Example 3: Address 0x0586 reads: 0x0066 is 1.02KW. Other references to 1st PV voltage, current and power
| 0585 -- 05B2 | Current_PV1 -- 16 |  | I16 | 0.01 | A |  |  | R | PV current for channels 1-16. Addresses start at 0x0585 and are spaced 3 addresses apart per circuit. | end user
| 0586 -- 05B3 | Power_PV1 -- 16 |  | U16 | 0.01 | kW |  |  | R | PV power for channels 1-16. Addresses start at 0x0586 and are spaced 3 addresses apart each way. | end user
| 05B4 -- 05B6 | [8 empty] | reserve
| 05C0 - 05C3 | AddressMask_Realtime_Input_PV2 |  | U64 |  |  |  |  | R | Mask area for the 64 register address words starting at this address. Refer to the description of address 0x0040 | end user | 0 | 0000000F
Total PV power | 05C4 | Power_PV_Total |  | U16 | 0.1 | kW |  |  | R | Total PV power. | end user | [6 empty] | The sum of all the PV power, read out the number of multiplication of precision that is the final data Example: 0x0007 means 0.7kw
2.5 Battery input (0x0600-0x067F) |  |  | Battery packs 1-12: voltage, charge/discharge current, charge/discharge power, ambient temperature, SOC, SOH, number of cycles and summary information
| 0600 -- 0603 | AddressMask_Realtime_Input_Bat1 |  | U64 |  |  |  |  | R | Mask area for the 64 register address words starting at this address. Refer to the description of address 0x0040 | end user | 0 | 0000000F
Battery packs 1-8 Data | 0604 -- 0635 | Voltage_Bat1 -- 8 |  | U16 | 0.1 | V |  |  | R | 1st-8th battery pack voltage. | end user | [6 empty] | The number of battery circuits depends on the specific model Each road is spaced 7 addresses apart. Read out the number multiplied by the precision that is the final data Charging and discharging current: charging is positive, discharging is negative. Example: 0x016C means 36.4V.
| 0605 -- 0636 | Current_Bat1 -- 8 |  | I16 | 0.01 | A |  |  | R | 1st - 8th way battery pack charge/discharge current. | end user
| 0606 -- 0637 | Power_Bat1 -- 8 |  | I16 | 0.01 | kW |  |  | R | Charge and discharge power of the 1st-8th battery packs. | end user
| 0607 -- 0638 | Temperature_Env_Bat1 -- 8 |  | I16 | 1 | ℃ |  |  | R | Ambient temperature of the 1st-8th battery packs. | end user | [6 empty] | Battery peripheral temperature, negative numbers indicate sub-zero temperatures. 7 addresses per circuit interval.
| 0608 -- 0639 | SOC_Bat1 -- 8 |  | U16 | 1 | % |  |  | R | 1st - 8th way battery pack SOC. | end user | [6 empty] | Battery level 7 addresses per circuit interval.
| 0609 -- 063A | SOH_Bat1 -- 8 |  | U16 | 1 | % |  |  | R | 1st - 8th way battery pack SOH. | end user | [6 empty] | Ability of the current battery to store electrical energy relative to a new battery 7 addresses per circuit interval.
| 060A -- 063B | ChargeCycle_Bat1 -- 8 |  | U16 | 1 | cycle |  |  | R | Number of cycles of the 1st-8th battery packs. | end user | [6 empty] | Number of battery charge/discharge cycles 7 addresses per circuit interval.
| 063C -- 063F | [8 empty] | reserve
| 0640 -- 0643 | AddressMask_Realtime_Input_Bat2 |  | U64 |  |  |  |  | R | Mask area for the 64 register address words starting at this address. Refer to the description of address 0x0040 | end user | 0 | 0000000F
Battery packs 1-8th circuit Data 1 | 0644 -- 0660 | Charge_Current_Limitation1 -- 8 |  | U16 | 0.01 | A |  |  | R | The upper limit of the charging current of the 1st-8th battery packs. | end user |  |  |  |  | The number of battery paths is related to the specific model Refer to the description of the 1st battery pack in the case 7 addresses per circuit interval |  | The number of battery paths is related to the specific model Refer to the description of the 1st battery pack in the case 7 addresses per circuit interval
| 0645 -- 0661 | Discharge_Current_limitation1 -- 8 |  | U16 | 0.01 | A |  |  | R | The upper limit of the discharge current of the 1st-8th battery packs. | end user
| 0646 -- 0662 | [7 empty] | R | Battery packs 1-8 are reserved. | end user
| 0647 -- 0663 | [7 empty] | R | Battery packs 1-8 are reserved. | end user
| 0664 -- 0666 | [8 empty] | reserve
Battery Pack Other data | 0667 | Power_Bat_Total |  | I16 | 0.1 | kW |  |  | R | Total battery charge and discharge power. Charging is positive, discharging is negative | end user
| 0668 | SOC_Bat_Average |  | U16 | 1 | % |  |  | R | Average of aggregated battery pack SOC | end user | [6 empty] | average power
| 0669 | SOH_Bat |  | U16 | 1 | % |  |  | R | Aggregate battery SOH | end user | [6 empty] | The ability of the current battery to store electrical energy relative to a new battery
| 066A | CurrentBattery_num |  | U16 | 1 |  |  |  | R | Real Time Battery Circuit
2.6 Power (0x0680-0x06BF) |  |  | Power information: power generation (day+total), load consumption (day+total), purchased power (day+total), sold power (day+total), battery charging (day+total), battery discharging (day+total)
| 0680 -- 0683 | AddressMask_Realtime_ElectricityStatistics1 |  | U64 |  |  |  |  | R | Mask area for the 64 register address words starting at this address. Refer to the description of address 0x0040 | end user | 0 | 0000000F
Electricity data | 0684 -- 0685 | PV_Generation_Today |  | U32 | 0.01 | kWh |  |  | R | Electricity generation for the day | end user | [6 empty] | The low address is the high bit, the high address is the low bit, read out the number multiplied by the precision that is the final data, for example: 0x0000 0x00EF said 2.39KWh
| 0686 -- 0687 | PV_Generation_Total |  | U32 | 0.1 | kWh |  |  | R | total generating capacity | end user | [6 empty] | The low address is the high bit, the high address is the low bit, read out the number multiplied by the precision that is the final data, for example: 0x0000 0x0017 said 2.3KWh
| 0688 -- 0689 | Load_Consumption_Today |  | U32 | 0.01 | kWh |  |  | R | Load Power Consumption of the Day | end user | [6 empty] | Low address is the high bit, high address is the low bit Read out the number multiplied by the precision is the final data Please refer to address 0x0684 and 0x0685 for examples.
| 068A -- 068B | Load_Consumption_Total |  | U32 | 0.1 | kWh |  |  | R | Total load power consumption | end user
| 068C -- 068D | Energy_Purchase_Today |  | U32 | 0.01 | kWh |  |  | R | Bought power for the day | end user
| 068E -- 068F | Energy_Purchase_Total |  | U32 | 0.1 | kWh |  |  | R | total purchased power | end user
| 0690 -- 0691 | Energy_Selling_Today |  | U32 | 0.01 | kWh |  |  | R | Electricity sales for the day | end user
| 0692 -- 0693 | Energy_Selling_Total |  | U32 | 0.1 | kWh |  |  | R | Total electricity sales | end user
| 0694 -- 0695 | Bat_Charge_Today |  | U32 | 0.01 | kWh |  |  | R | Battery charge of the day | end user
| 0696 -- 0697 | Bat_Charge_Total |  | U32 | 0.1 | kWh |  |  | R | Total Battery Charge | end user
| 0698 -- 0699 | Bat_Discharge_Today |  | U32 | 0.01 | kWh |  |  | R | Battery discharge for the day | end user
| 069A -- 069B | Bat_Discharge_Total |  | U32 | 0.1 | kWh |  |  | R | Total Battery Discharge | end user
Current month of the year Electricity data | 069C -- 069D | PV_Generation_Month |  | U32 | 0.1 | kWh |  |  | R | Electricity generation for the month | end user
| 069E -- 069F | PV_Generation_Year |  | U32 | 0.1 | kWh |  |  | R | Current year's electricity generation | end user
| 06A0 -- 06A1 | Load_Consumption_Month |  | U32 | 0.1 | kWh |  |  | R | Load Power Consumption for the Month | end user
| 06A2 -- 06A3 | Load_Consumption_Year |  | U32 | 0.1 | kWh |  |  | R | Current Year Load Power Consumption | end user
| 06A4 -- 06A5 | Energy_Purchase_Month |  | U32 | 0.1 | kWh |  |  | R | Electricity purchased this month | end user
| 06A6 -- 06A7 | Energy_Purchase_Year |  | U32 | 0.1 | kWh |  |  | R | Electricity purchased during the year | end user
| 06A8 -- 06A9 | Energy_Selling_Month |  | U32 | 0.1 | kWh |  |  | R | Electricity sales for the month | end user
| 06AA -- 06AB | Energy_Selling_Year |  | U32 | 0.1 | kWh |  |  | R | Electricity sales for the year | end user
| 06AC -- 06AD | Bat_Charge_Month |  | U32 | 0.1 | kWh |  |  | R | Battery Charge of the Month | end user
| 06AE -- 06AF | Bat_Charge_Year |  | U32 | 0.1 | kWh |  |  | R | Battery charge for the year | end user
| 06B0 -- 06B1 | Bat_Discharge_Month |  | U32 | 0.1 | kWh |  |  | R | Battery discharge for the month | end user
| 06B2 -- 06B3 | Bat_Discharge_Year |  | U32 | 0.1 | kWh |  |  | R | Battery discharge for the year | end user
2.7 Internal Information (0x06C0-0x06FF) |  |  | Leakage Current, Balance Current, R/S/T Current DC Component, Total BUS Voltage, PV1-16 Flying Across Capacitor Voltage, Rated Power, IV Scan RMS Points, etc.
| 06C0 -- 06C3 | AddressMask_Realtime_ClassifiedInfo1 |  | U64 |  |  |  |  | R | Mask area for the 64 register address words starting at this address. Refer to the description of address 0x0040 | installer | 0 | 0000000F
leakage current | 06C4 | GFCI |  | U16 | 1 | mA |  |  | R | leakage current | installer | [6 empty] | Example: 0x0005 means 5mA
equilibrium current | 06C5 | Current_Bus_Balance |  | I16 | 0.01 | A |  |  | R | equilibrium current | installer | [6 empty] | Note: Achieving three-phase balancing
DC component | 06C6 | DCI_R |  | I16 | 1 | mA |  |  | R | R phase current DC component | installer
| 06C7 | DCI_S |  | I16 | 1 | mA |  |  | R | S-phase current DC component | installer
| 06C8 | DCI_T |  | I16 | 1 | mA |  |  | R | T-phase current DC component | installer
| 06C9 | DCV_R |  | I16 | 1 | mV |  |  | R | R phase voltage DC component | installer
| 06CA | DCV_S |  | I16 | 1 | mV |  |  | R | S phase voltage DC component | installer
| 06CB | DCV_T |  | I16 | 1 | mV |  |  | R | T-phase voltage DC component | installer
BUS Voltage Information BuckBoost Current | 06CC | Voltage_Bus |  | U16 | 0.1 | V |  |  | R | Total BUS voltage | installer | [6 empty] | bus voltage, the inverter will step up the input voltage of the PV to the BUS voltage to meet the inverter requirements, and then invert the
| 06CD | Voltage_Bus_P |  | U16 | 0.1 | V |  |  | R | BUS Positive Voltage | installer | [6 empty] | bus+, positive voltage to ground
| 06CE | Voltage_Bus_N |  | U16 | 0.1 | V |  |  | R | BUS Negative Voltage | installer | [6 empty] | bus-,negative voltage to ground
| 06CF | Voltage_Bus_LLC |  | U16 | 0.1 | V |  |  | R | LLC Bus Voltage | installer
| 06D0 | Current_BuckBoost |  | I16 | 0.01 | A |  |  | R | BuckBoost Current | installer
| 06D1 | Voltage_Bus_P_Half |  | U16 | 0.1 | V |  |  | R | BUS positive half voltage | installer
| 06D2 | Voltage_Bus_N_Half |  | U16 | 0.1 | V |  |  | R | BUS negative half voltage | installer
Fly across capacitor voltage | 06D3 -- 06E2 | FlyingCap_Voltage1 -- 16 |  | U16 | 0.1 | V |  |  | R | PV1-16 fly across capacitor voltages (16) | installer
Internal information | 06E3 -- 06EC | Internal_Info1 -- 10 |  | U16 | 0.1 | V |  |  | R | Internal messages 1-10 (10, debugging information area) | installer
Inverter Rated Power | 06ED | RatedPower_Inverter |  | U16 | 0.1kW | kW |  |  | R | Inverter Rated Power | installer
IV curve scanning | 06EE | IVPoints_Effec_Num |  | U16 | 1 |  | 1 | 150 | R | Number of valid points for IV curve scanning | installer
BUS negative voltage to ground | 06EF | Voltage_Bus_N_GND |  | I16 | 0.1 | V |  |  | R | BUS negative voltage to ground | installer | [7 empty] | Ground power station225KTL-HV
Equipment Information | 06FC | ProjectNum | R | U16 * 1 | [5 empty] | Project designator to distinguish the region's data definitions, enumeration type: 0: 0-225KTLX-HV Item; Other-Reserve
Reservation for equipment control | 06FD~06FF | reserved | RW | U16 * 3 | [5 empty] | Reserved, readout is 0
2.8 Sink Information (0x0700-0x077F) |  |  | Group 1-16 sink voltage, 1-4 way string current, model-related
| 0700 -- 0703 | AddressMask_Realtime_CombinerInfo1 |  | U64 |  |  |  |  | R | Mask area for the 64 register address words starting at this address. Refer to the description of address 0x0040 | installer | 0 | 0000000F
Groups 1-16 Sink Voltage String Current | 0704 -- 0731 | Voltage_Group1 -- 16 |  | U16 | 0.1 | V |  |  | R | Groups 1-16 sink voltage (16). | [7 empty] | Equal to PV1 voltage, addresses start at 0x0704, 3 addresses per group interval. Example: 0x0866 indicates 215V
| 0705 -- 0732 | Current_Group1_Branch1 -- Current_Group16_Branch1 |  | I16 | 0.01 | A |  |  | R | Groups 1-16 Group 1 string currents (16). | [7 empty] | Equal to PV1 current, address starts at 0x0705, each group is spaced 3 addresses apart, note that there is also a 3rd-4th string current, address starts at 0x0744. Example: 0x015F means 3.51A
| 0706 -- 0733 | Current_Group1_Branch2 -- Current_Group16_Branch2 |  | I16 | 0.01 | A |  |  | R | Group 1-16 Group 2 string currents (16). | [7 empty] | Whether or not this function is available is related to the model, case reference group 1 1st string current, address starts from 0x0706, 3 addresses per group interval, note that there is also 3rd-4th string current, address starts from 0x0744.
| 0734 -- 073F | [8 empty] | reserve
| 0740 -- 0743 | AddressMask_Realtime_CombinerInfo2 |  | U64 |  |  |  |  | R | Mask area for the 64 register address words starting at this address. Refer to the description of address 0x0040 | installer | 0 | 0000000F
Groups 1-16 Sink current String Current | 0744 -- 0762 | Current_Group1_Branch3 -- Current_Group16_Branch3 |  | I16 | 0.01 | A |  |  | R | Group 1-16 3rd way string current (16). | [7 empty] | The availability of this function depends on the model Case reference group 1 group 1 way string current Each group is spaced 2 addresses apart.
| 0745 -- 0763 | Current_Group1_Branch4 -- Current_Group16_Branch4 |  | I16 | 0.01 | A |  |  | R | Group 1-16 4th way string current (16).
| 0764 -- 077F | [8 empty] | reserve
2.9 Pull arc information (0x0780-0x07C8) The function of this block address is not used for the time being |  |  | MPPT1-24-way monitoring real-time arc intensity, historical maximum value, arc partial extreme value
| 0780 -- 0783 | AddressMask_Realtime_ArcInfo3 |  | U64 |  |  |  |  | R | Mask area for the 64 register address words starting at this address. Refer to the description of address 0x0040 | installer | 0 | 0000000F
Real-time arc intensity | 0784 -- 079B | ArcStrength_MPPT_1 -- 24 |  | I16 | 1 |  |  |  | R | MPPT 1 - 24 monitored real-time arc intensity (24)
| 079C - 07A1 | [8 empty] | reserve
Historical Arc Intensity Values | 07A2 -- 07B9 | ArcStrength_history_Channel1 -- 24 |  | I16 | 1 |  |  |  | R | Channels 1 - 24 Record historical maximum value of monitored arc intensity after power-up, automatically cleared after power-down (24)
| 07BA -- 07BF | [8 empty] | reserve
| 07C0 -- 07C3 | AddressMask_Realtime_ArcInfo4 |  | U64 |  |  |  |  | R | Mask area for the 64 register address words starting at this address. Refer to the description of address 0x0040 | installer | 0 | 0000000F
arc limit value (math.) | 07C4 | arc_peak_to_peak |  | U16 | 1 |  |  |  | R | Maximum peak-to-peak value of the arc
| 07C5 | arc_variance |  | U16 | 1 |  |  |  | R | Arc maximum variance
| 07C6 | arc_harmonic_energy |  | U16 | 1 |  |  |  | R | Maximum harmonic energy of the arc
| 07C7 | arc_amplitude_variance |  | U16 | 1 |  |  |  | R | Arc maximum magnitude variance
III. Safety parameter area (0x0800-0x0FFF)
3.1 Power-up parameters (0x0800-0x083F)
| 0800 | ConnectWaitTime |  | U16 | 1 | unit of angle or arc equivalent one sixtieth of a degree | 1 | 65535 | RW | Waiting time before grid connection | installer | [6 empty] | This interface registers are independent of each other for setting parameter functions.
| 0801 | PowerUpSpeed |  | U16 | 1 | %Pn/min | 1 | 3000 | RW | 100 indicates the rate corresponding to the 1-minute rise to full load, and other values are calculated by multiplying and dividing on this basis Note: Grid-connected rise rate | installer
| 0802 | ReconnectWaitTime |  | U16 | 1 | unit of angle or arc equivalent one sixtieth of a degree | 1 | 65535 | RW | Waiting time before reconnection to the grid after grid fault recovery | installer
| 0803 | ReconnectPowerUpSpeed |  | U16 | 1 | %Pn/min | 1 | 3000 | RW | 100 indicates the rate corresponding to a 1-minute rise to full load, and other values are calculated by multiplying and dividing on this basis Note: Rise rate after grid fault recovery | installer
| 0804 | VoltHighLimit |  | U16 | 0.1 | V | 0 | 65535 | RW | Note: The voltage at grid startup cannot exceed this setting. | end user
| 0805 | VoltLowLimit |  | U16 | 0.1 | V | 0 | 65535 | RW | Lower limit of startup grid voltage Note: The voltage at startup of the grid cannot be lower than this setting value | end user
| 0806 | FreqHighLimit |  | U16 | 0.01 | Hz | 4000 | 7000 | RW | Activation of the upper limit of the grid frequency | end user
| 0807 | FreqLowLimit |  | U16 | 0.01 | Hz | 4000 | 7000 | RW | Starting grid frequency lower limit | end user
| 0808 | ReconnectVoltHighLimit |  | U16 | 0.1 | V | 0 | 65535 | RW | Reconnecting to the grid voltage limit | end user
| 0809 | ReconnectVoltLowLimit |  | U16 | 0.1 | V | 0 | 65535 | RW | Reconnecting the grid voltage lower limit | end user
| 080A | ReconnectFreqHighLimit |  | U16 | 0.01 | Hz | 4000 | 7000 | RW | Note: The voltage frequency during reconnection startup cannot exceed this setting. | end user
| 080B | ReconnectFreqLowLimit |  | U16 | 0.01 | Hz | 4000 | 7000 | RW | Lower limit of reconnection grid frequency Note: The voltage and frequency at reconnection startup cannot be lower than this setting. | end user
3.2 Voltage protection parameters (0x0840-0x087F)
| 0840 | Voltage Config |  | U16 |  |  |  |  | RW | Bit0: overvoltage primary protection enable bit Bit1: over-voltage secondary protection enable bit Bit2: over-voltage three-level protection enable bit Bit3: undervoltage primary protection enable bit Bit4: undervoltage secondary protection enable bit Bit5: under-voltage three-level protection enable bit Bit6: 10-minute over-voltage protection enable bit Note: Setting 1 for enable is on, setting 0 is off. | installer | [6 empty] | The overvoltage one/two/three level protection enable bits control the one/two/three level overvoltage protection value and the one/two/three level overvoltage protection time respectively. The undervoltage one/two/three level protection enable bits control the one/two/three level undervoltage protection value and the one/two/three level undervoltage protection time, respectively. 10-minute overvoltage protection enable bits control the 10-minute overvoltage protection value of the power grid. Only when the enable bit is turned on, the function of the corresponding register can be reflected.
| 0841 | RatedVoltage |  | U16 | 0.1 | V | 0 | 65535 | RW | Rated grid voltage | installer
| 0842 | FirstOvervoltageProtectionValue |  | U16 | 0.1 | V | 0 | 65535 | RW | First-stage overvoltage protection value Note: Set first-stage voltage protection threshold, exceeding the trigger protection mechanism | end user
| 0843 | FirstOvervoltageProtectionTime |  | U16 | 10 | ms | 1 | 65535 | RW | First-stage overvoltage protection time Note: Set first-stage voltage time threshold, exceeding triggers the protection mechanism | installer
| 0844 | SecondOvervoltageProtectionValue |  | U16 | 0.1 | V | 0 | 65535 | RW | Secondary overvoltage protection value | end user
| 0845 | SecondOvervoltageProtectionTime |  | U16 | 10 | ms | 1 | 65535 | RW | Secondary overvoltage protection time | installer
| 0846 | ThirdOvervoltageProtectionValue |  | U16 | 0.1 | V | 0 | 65535 | RW | Three-level overvoltage protection value | end user
| 0847 | ThirdOvervoltageProtectionTime |  | U16 | 10 | ms | 1 | 65535 | RW | Three-stage overvoltage protection time | installer
| 0848 | FirstUnderVoltageProtectionValue |  | U16 | 0.1 | V | 0 | 65535 | RW | Primary undervoltage protection value | end user
| 0849 | FirstUndervoltageProtectionTime |  | U16 | 10 | ms | 1 | 65535 | RW | Primary undervoltage protection time | installer
| 084A | SecondUnderVoltageProtectionValue |  | U16 | 0.1 | V | 0 | 65535 | RW | Secondary undervoltage protection value | end user
| 084B | SecondUndervoltageProtectionTime |  | U16 | 10 | ms | 1 | 65535 | RW | Secondary undervoltage protection time | installer
| 084C | ThirdUnderVoltageProtectionValue |  | U16 | 0.1 | V | 0 | 65535 | RW | Three-level undervoltage protection value | end user
| 084D | ThirdUndervoltageProtectionTime |  | U16 | 10 | ms | 1 | 65535 | RW | Three-stage undervoltage protection time | installer
| 084E | 10MinOvervoltageProtectionValue |  | U16 | 0.1 | V | 0 | 65535 | RW | Grid 10-minute overvoltage protection value | installer
| 084F | FirstOvervoltageProtectionTimeHi |  | U16 |  |  | 0 | 255 | RW | Primary overvoltage protection time high | installer | [6 empty] | Note: This register is used in combination with the first level of overvoltage protection time to form a 32-bit register
| 0850 | SecondOvervoltageProtectionTimeHi |  | U16 |  |  | 0 | 255 | RW | Secondary overvoltage protection time high | installer | [6 empty] | Note: This register is used in combination with the secondary overvoltage protection time as a 32-bit register
| 0851 | ThirdOvervoltageProtectionTimeHi |  | U16 |  |  | 0 | 255 | RW | Three-stage overvoltage protection time high | installer | [6 empty] | Note: This register is used in combination with the three-stage overvoltage protection time to form a 32-bit register
3.3 Frequency protection parameters (0x0880-0x08BF)
| 0880 | FrequencyConfig |  | U16 |  |  |  |  | RW | Bit0 Overclocking primary protection enable bit Bit1 Overfrequency secondary protection enable bit Bit2 Overfrequency third level protection enable bit Bit3 Underfrequency primary protection enable bit Bit4 Underfrequency secondary protection enable bit Bit5 Underfrequency third level protection enable bit Bit6 Frequency change rate protection enable bit Note: Setting 1 for enable is on, setting 0 is off. | installer | [6 empty] | The overfrequency one/two/three protection enable bits control the one/two/three overfrequency protection value and the one/two/three overfrequency protection time, respectively. The underfrequency one/two/three protection enable bits control one/two/three underfrequency protection values and one/two/three underfrequency protection times, respectively. Only when the enable bit is turned on, the function of the corresponding register can be reflected.
| 0881 | RatedFrequency |  | U16 | 0.01 | Hz | 4000 | 7000 | RW | Rated grid frequency | installer
| 0882 | FirstOverfrequencyProtectionValue |  | U16 | 0.01 | Hz | 4000 | 7000 | RW | A level of over-frequency protection value Note: A level of frequency protection threshold, over the trigger protection mechanism | end user
| 0883 | FirstOverfrequencyProtectionTime |  | U16 | 10 | ms | 1 | 65535 | RW | A level of over-frequency protection time Note: A level of frequency time protection threshold, more than the trigger protection mechanism | installer
| 0884 | SecondOverfrequencyProtectionValue |  | U16 | 0.01 | Hz | 4000 | 7000 | RW | Secondary overfrequency protection value | end user
| 0885 | SecondOverfrequencyProtectionTime |  | U16 | 10 | ms | 1 | 65535 | RW | Secondary overfrequency protection time | installer
| 0886 | ThirdOverfrequencyProtectionValue |  | U16 | 0.01 | Hz | 4000 | 7000 | RW | Three-level overfrequency protection value | end user
| 0887 | ThirdOverfrequencyProtectionTime |  | U16 | 10 | ms | 1 | 65535 | RW | Three-stage overfrequency protection time | installer
| 0888 | FirstUnderfrequencyProtectionValue |  | U16 | 0.01 | Hz | 4000 | 7000 | RW | Primary underfrequency protection value | end user
| 0889 | FirstUnderfrequencyProtectionTime |  | U16 | 10 | ms | 1 | 65535 | RW | Primary underfrequency protection time | installer
| 088A | SecondUnderfrequencyProtectionValue |  | U16 | 0.01 | Hz | 4000 | 7000 | RW | Secondary underfrequency protection value | end user
| 088B | SecondUnderfrequencyProtectionTime |  | U16 | 10 | ms | 1 | 65535 | RW | Secondary underfrequency protection time | installer
| 088C | ThirdUnderfrequencyProtectionValue |  | U16 | 0.01 | Hz | 4000 | 7000 | RW | Three-level underfrequency protection value | end user
| 088D | ThirdUnderfrequencyProtectionTime |  | U16 | 10 | ms | 1 | 65535 | RW | Three levels of underfrequency protection time | installer
| 088E | FirstOverfrequencyProtectionTimeHi |  | U16 |  |  | 0 | 255 | RW | Primary overfrequency protection time high | [7 empty] | Note: This register is used in combination with the first level of over-frequency protection time to form a 32-bit register
| 088F | SecondOverfrequencyProtectionTimeHi |  | U16 |  |  | 0 | 255 | RW | Secondary overfrequency protection time high | [7 empty] | Note: This register is used in combination with the secondary overclocking protection time as a 32-bit register
| 0890 | ThirdOverfrequencyProtectionTimeHi |  | U16 |  |  | 0 | 255 | RW | Three-stage overfrequency protection time high | [7 empty] | Note: This register is used in combination with the three-stage overclocking protection time to form a 32-bit register
| 0891 | FirstUnderfrequencyProtectionTimeHi |  | U16 |  |  | 0 | 255 | RW | Primary underfrequency protection time high | [7 empty] | Note: This register is used in combination with the first level underfrequency protection time to form a 32-bit register
| 0892 | SecondUnderfrequencyProtectionTimeHi |  | U16 |  |  | 0 | 255 | RW | Secondary underfrequency protection time high | [7 empty] | Note: This register is used in combination with the secondary underfrequency protection time as a 32-bit register
| 0893 | ThirdUnderfrequencyProtectionTimeHi |  | U16 |  |  | 0 | 255 | RW | Three levels of underfrequency protection time high | [7 empty] | Note: This register is used in combination with the three levels of underclocking protection time to form a 32-bit register
| 0894 | RoCoFMaxLimit |  | U16 | 0.01 | Hz/s | 100 | 1000 | RW | Frequency change rate protection value | end user
| 0895 | RoCoFMaxProtectTime |  | U16 | 10 | ms | 1 | 65535 | RW | Frequency rate of change protection time | end user
3.4 DCI protection parameters (0x08C0-0x08FF)
| 08C0 | DCI Config |  | U16 |  |  |  |  | RW | Bit0: DCI primary protection enable bit Bit1: DCI secondary protection enable bit Bit2: DCI three-level protection enable bit Bit3: DCI test enable bit Note: enable is set to 1 for on, set to 0 for off | installer | [6 empty] | The DCI I/II/III protection enable bits control the DCI I/II/III protection value and DCI I/II/III protection time respectively. The DCI test enable bit controls the DCI (R, S, T) three-phase test value. Only when the enable bit is turned on, the function of the corresponding register can be reflected.
| 08C1 | DCIFirstProtectionValue |  | U16 | 1 | mA | 1 | 65535 | RW | DCI primary protection value | installer | [6 empty] | Note: DC component level 1 protection threshold, exceeding the trigger protection mechanism
| 08C2 | DCIFirstProtectionTime |  | U16 | 10 | ms | 1 | 65535 | RW | DCI primary protection time | installer | [6 empty] | Note: DC component level 1 time protection threshold, exceeding the trigger protection mechanism
| 08C3 | DCISecondProtectionValue |  | U16 | 1 | mA | 1 | 65535 | RW | DCI secondary protection value | installer
| 08C4 | DCISecondProtectionTime |  | U16 | 10 | ms | 1 | 65535 | RW | DCI secondary protection time | installer
| 08C5 | DCIThirdProtectionValue |  | U16 | 1 | mA | 1 | 65535 | RW | DCI Level 3 protection value | installer
| 08C6 | DCIThirdProtectionTime |  | U16 | 10 | ms | 1 | 65535 | RW | DCI Level 3 protection time | installer
| 08C7 | DCITestValue1 |  | I16 | 1 | mA | -32768 | 32767 | RW | DCI R-phase test value | installer | [6 empty] | Note: DC component R phase test set value
| 08C8 | DCITestValue2 |  | I16 | 1 | mA | -32768 | 32767 | RW | DCI S-phase test value | installer
| 08C9 | DCITestValue3 |  | I16 | 1 | mA | -32768 | 32767 | RW | DCI T-phase test values | installer
| 08CA | DCIFirstProtectionProportion |  | U16 | 0.01 | % | 1 | 65535 | RW | DCI primary protection ratio | installer | [6 empty] | Note: DC component first level protection ratio
| 08CB | DCISecondProtectionProportion |  | U16 | 0.01 | % | 1 | 65535 | RW | DCI secondary protection ratio | installer
| 08CC | DCIThirdProtectionProportion |  | U16 | 0.01 | % | 1 | 65535 | RW | DCI three-level protection ratio | installer
3.5 Active, over-undervoltage derating parameters (0x0900-0x093F)
| 0900 | Remote Config |  | U16 |  |  |  |  | RW | Bit0: active load shedding enable bit Bit1: Remote on/off enable bit Bit2: over-voltage load shedding enable bit Bit3: Over-voltage charging power-down enable bit Bit4: under-voltage charging power-down enable bit Bit5: DRM0 enable bit Bit6: Logic interface (DRM1-8) enable bit Bit7: Anti-reverse current overload enable bit Bit8: Voltage drop load PT curve enable bit Bit9: Remote shutdown load shedding enable bit (0: default direct shutdown, 1: ramp load shedding shutdown) Bit10: CLS anti-reverse current enable bit Note: Enable is set 1 for on, set 0 for off | installer | [6 empty] | The active load shedding enable bit controls the active output percentage and the active load shedding rate The remote on/off enable bit controls the remote on/off switching. The overvoltage derating enable bit controls the grid overvoltage derating start/end/cutoff power and overvoltage derating rate. The undervoltage buck charging power enable bit controls the grid undervoltage buck start/end/cutoff power. The Voltage Drop PT Curve enable bit controls the voltage drop time. Logic interface enable bit controls the corresponding power of logic interface (1-8). The anti-reverse current overload enable bit controls the anti-reverse current power, anti-reverse current overload time, logical interface load-down rate, and logical interface load-back rate. Only when the enable bit is turned on, the function of the corresponding register can be reflected.
| 0901 | ActiveOutputLimit |  | U16 | 0.1 | % | 0 | 1000 | RW | Percentage of active output | installer
| 0902 | ActiveOutputDownSpeed |  | U16 | 1 | %Pn/min | 1 | 300 | RW | Active load shedding rate
| 0903 | GridVoltageDropStart |  | U16 | 0.1 | V | 0 | 65535 | RW | Starting point of overvoltage load shedding in the grid | installer
| 0904 | GridVoltageDropStop |  | U16 | 0.1 | V | 0 | 65535 | RW | Grid overvoltage load shedding termination point | installer
| 0905 | GridVoltageDropMinPower |  | I16 | 1 | % | -100 | 100 | RW | Grid overvoltage load shedding cutoff power | installer
| 0906 | OvervoltageDownSpeed |  | U16 | 1 | %Pn/min | 1 | 300 | RW | Overvoltage derating rate | installer
| 0907 | ChgDerateVoltStart |  | U16 | 0.1 | V | 0 | 65535 | RW | Starting point of grid undervoltage load shedding | installer
| 0908 | ChgDerateVoltEnd |  | U16 | 0.1 | V | 0 | 65535 | RW | Grid undervoltage load shedding termination point | installer
| 0909 | ChgDerateMinPower |  | I16 | 1 | % | -100 | 100 | RW | Grid undervoltage load shedding cut-off power | installer
| 090A -- 0911 | PowerForLogic1 -- 8 |  | I16 | 1 | % | -100 | 100 | RW | Logic interfaces 1-8 corresponding to power (8) | installer
| 0912 | RefluxPower |  | U16 | 1 | % | 0 | 100 | RW | Anti-reverse current power (VDE4105 safety regulation grid-connected power limit) | installer
| 0913 | RefluxOVloadTime |  | U16 | 10 | ms | 0 | 65535 | RW | Anti-reverse current overload time (VDE4105 safety regulation reverse current overload off-grid time) | installer
| 0914 | LogicDerateSpeed |  | U16 | 1 | %Pn/min | 1 | 65535 | RW | logical interface down load rate | installer
| 0915 | LogicReloadSpeed |  | U16 | 1 | %Pn/min | 1 | 65535 | RW | logical interface slew rate | installer
| 0916 | VoltageDerateResponseTime |  | U16 | 1 | unit of angle or arc equivalent one sixtieth of a degree | 0 | 65535 | RW | Voltage dropout time | installer
| 0917 | PowerDownSpeed |  | U16 | 1 | %Pn/min | 1 | 3000 | RW | Remote shutdown load shedding rate | installer
| 0918 | CLSRemote Config |  | U16 |  |  |  |  | RW | Bit0: CLS household device selection bit (0: household device, 1: non-household device); Bit1: CLS low power state lock enable bit (low power: current limited to 0.1% of rated current); Bit2: CLS low power state can be automatically recovered enable bit; Other bits are reserved; | installer
| 0919 | CLSExportCurrentLimit |  | U16 | 1 | % | 0 | 100 | RW | CLS Anti-Reverse Current Output Current Limit Percentage | installer
| 091A | CLSImportCurrentLimit |  | U16 | 1 | % | 0 | 100 | RW | CLS Anti-Reverse Current Input Current Limit Percentage | installer
| 091B | CLSCurrentLimitTime |  | U16 | 10 | ms | 1 | 65535 | RW | CLS Anti-reverse current PCC current limit time | installer
| 091C | CLSCurrentProtectTime |  | U16 | 10 | ms | 1 | 65535 | RW | CLS Anti-reverse current PCC current protection time | installer
3.6 Over-underfrequency load shedding parameters (0x0940-0x097F)
| 0940 | FrequencyDerateConfig |  | U16 |  |  |  |  | RW | Bit0: overfrequency output load-down enable Bit1: under-frequency input load-down enableBit2: overfrequency load return enable with frequency Bit3: underfrequency load back with frequency enable Bit4: overfrequency load shedding from rated power enable Bit5：calculate load shedding slope with current power enable Bit6: Energy storage segment curve enable Bit7: Maximum power calculation enable Bit8: Underfrequency derating from rated power enableBit9: Over underfrequency load return rate with frequency enable bit Bit12-13: Load-down mode (0 slope mode/1 frequency range mode) Bit14: Over-frequency load shedding power cut-off enable bit Note: 225kw PV models do not support storage segmentation curve enable and maximum power calculation enable functions. Note: 225kw model from the rated power start load shedding enable and current power calculation load shedding slope enable this interface can not be reflected Note: This parameter interface area is divided into two major interfaces of the photovoltaic and energy storage Note: Enable for set 1 for on, set 0 for off | installer | [6 empty] | The overfrequency output load-down enable controls the load-down mode (0 slope mode/1 frequency range mode), 0 slope mode controls the overfrequency load-down (start frequency/slope percentage/startup wait time), and 1 frequency range mode controls the overfrequency load-down (start frequency/cutoff frequency/startup wait time). The underfrequency input load shedding enable controls the underfrequency load shedding start frequency/cutoff frequency/slope percentage/startup wait time. The overfrequency loadback enable controls the overfrequency loadback wait time/overfrequency loadback frequency/overfrequency loadback cutoff rate percentage. Underfrequency Loadback Enable controls Underfrequency Loadback Waiting Time/Underfrequency Dropped Loadback Frequency/Underfrequency Loadback Cutoff Rate Percentage and Exit Dropped Load Highest/Lowest Frequency. Only when the enable bit is turned on, the function of the corresponding register can be reflected.
| 0941 | OverfrequencyStart |  | U16 | 0.01 | Hz | 4000 | 7000 | RW | Starting frequency of overfrequency load shedding | installer
| 0942 | OverfrequencyEnd |  | U16 | 0.01 | Hz | 4000 | 7000 | RW | Overfrequency load shedding cutoff frequency. Frequency range mode valid | installer
| 0943 | OverfrequencySlope |  | U16 | 1 | %Pn/Hz | 1 | 300 | RW | Percentage of overfrequency load shedding slope. Slope mode is valid German standard slope=1/(s*fn) | installer
| 0944 | OverfrequencyResponseDelay |  | U16 | 10 | ms | 0 | 65535 | RW | Overclocking load shedding startup wait time | installer
| 0945 | OverfrequencyReloadDelay |  | U16 | 10 | ms | 0 | 65535 | RW | Waiting time before overfrequency reload | installer
| 0946 | OverfrequencyReloadStart |  | U16 | 0.01 | Hz | 4000 | 7000 | RW | Overfrequency load shedding backload frequency. Effective when overfrequency backloading is prohibited. | installer
| 0947 | OverfrequencyReloadSpeed |  | U16 | 1 | %Pn/min | 1 | 300 | RW | Percentage of overfrequency return rate | installer
| 0948 | UnderfrequencyStart |  | U16 | 0.01 | Hz | 4000 | 7000 | RW | Starting frequency of underfrequency load shedding | installer
| 0949 | UnderfrequencyEnd |  | U16 | 0.01 | Hz | 4000 | 7000 | RW | Underfrequency dropout cutoff frequency. Frequency range mode valid | installer
| 094A | UnderfrequencySlope |  | U16 | 1 | %Pn/Hz | 1 | 300 | RW | Percentage of underclocked load shedding slope. Slope mode is valid | installer
| 094B | UnderfrequencyResponseDelay |  | U16 | 10 | ms | 0 | 65535 | RW | Waiting time for underfrequency load shedding startup | installer
| 094C | UnderfrequencyReloadDelay |  | U16 | 10 | ms | 0 | 65535 | RW | Waiting time before underfrequency reload | installer
| 094D | UnderfrequencyReloadStart |  | U16 | 0.01 | Hz | 4000 | 7000 | RW | Underfrequency load shedding backload frequency. Effective when underfrequency backloading is prohibited. | installer
| 094E | UnderfrequencyReloadSpeed |  | U16 | 1 | %Pn/min | 1 | 300 | RW | Percentage of underfrequency return rate | installer
| 094F | FrequencyRecoverMax |  | U16 | 0.01 | Hz | 4000 | 7000 | RW | Exit load shedding maximum frequency. Over and Under Frequency Sharing. Effective when overfrequency backloading is allowed | installer
| 0950 | FrequencyRecoverMin |  | U16 | 0.01 | Hz | 4000 | 7000 | RW | Exit load shedding minimum frequency. Over Underfrequency Sharing. Effective when underfrequency backloading is allowed | installer
| 0951 | ESSOverFrequencyStart |  | U16 | 0.01 | Hz | 4000 | 7000 | RW | （Starting frequency of over-frequency load shedding (energy storage) | installer
| 0952 | ESSOverfrequencyEnd |  | U16 | 0.01 | Hz | 4000 | 7000 | RW | (Energy storage) Overfrequency load shedding cutoff frequency. Frequency range mode valid
| 0953 | ESSOverFrequencySlope |  | U16 | 1 | %Pn/Hz | 1 | 300 | RW | (Energy Storage) Percentage of over-frequency load shedding ramp. Slope mode is valid German standard slope=1/(s*fn) | installer
| 0954 | ESSOverFrequencyResponseDelay |  | U16 | 10 | ms | 0 | 65535 | RW | （Waiting time for overfrequency load shedding startup (energy storage) | installer
| 0955 | ESSOverFrequencyReloadDelay |  | U16 | 10 | ms | 0 | 65535 | RW | （Waiting time before overfrequency load return (energy storage) | installer
| 0956 | ESSOverfrequencyReloadStart |  | U16 | 0.01 | Hz | 4000 | 7000 | RW | (Energy storage) Overfrequency load shedding return frequency. Effective when overfrequency load return is prohibited. | installer
| 0957 | ESSOverFrequencyReloadSpeed |  | U16 | 1 | %Pn/min | 1 | 300 | RW | （Percentage of over-frequency return rate (energy storage) | installer
| 0958 | ESSUnderFrequencyExprotStart |  | U16 | 0.01 | Hz | 4000 | 7000 | RW | （Starting frequency of under-frequency load shedding discharge (energy storage) | installer
| 0959 | ESSUnderfrequencyEnd |  | U16 | 0.01 | Hz | 4000 | 7000 | RW | (Energy storage) Underfrequency load shedding cutoff frequency. Frequency range mode active
| 095A | ESSUnderFrequencySlope |  | U16 | 1 | %Pn/Hz | 1 | 300 | RW | (Energy Storage) Underfrequency load shedding slope percentage. Ramp mode is valid | installer
| 095B | ESSUnderFrequencyResponseDelay |  | U16 | 10 | ms | 0 | 65535 | RW | （Waiting time for underfrequency load shedding startup (energy storage) | installer
| 095C | ESSUnderFrequencyReloadDelay |  | U16 | 10 | ms | 0 | 65535 | RW | （Waiting time before underfrequency load return (energy storage) | installer
| 095D | ESSUnderfrequencyReloadStart |  | U16 | 0.01 | Hz | 4000 | 7000 | RW | (Energy storage) Underfrequency load shedding backload frequency. Effective when underfrequency loadback is prohibited. | installer
| 095E | ESSUnderFrequencyReloadSpeed |  | U16 | 1 | %Pn/min | 1 | 300 | RW | （Percentage of underfrequency backloading rate (energy storage) | installer
| 095F | ESSFrequencyRecoverMax |  | U16 | 0.01 | Hz | 4000 | 7000 | RW | (Energy storage) Exit load shedding maximum frequency. Over-underfrequency sharing | installer
| 0960 | ESSFrequencyRecoverMin |  | U16 | 0.01 | Hz | 4000 | 7000 | RW | (Energy storage) Exit load shedding minimum frequency. Over-underfrequency sharing | installer
| 0961 | ESSOverFrequencyTransition |  | U16 | 0.01 | Hz | 4000 | 7000 | RW | (Energy Storage) Overfrequency derating power traversal frequency point. Valid when 0940 Bit6 is enabled. | installer
| 0962 | ESSUnderFrequencyTransition |  | U16 | 0.01 | Hz | 4000 | 7000 | RW | (Energy Storage) Underfrequency derated power crossing frequency point. Valid when 0940 Bit6 is enabled. | installer
| 0963 | ESSUnderFrequencyImportStart |  |  |  | Hz | 4000 | 7000 | RW | （Starting frequency of underfrequency load shedding charging (energy storage) | installer
3.7 Reactive power parameters (0x0980-0x09BF)
| 0980 | ReactiveConfig |  | U16 |  |  |  |  | RW | Bit0: Reactive Enable Bit1-3: reactive mode Bit8: reactive mode three-voltage entry enable bit Bit9: charging reactive enable Bit10: reactive mode four Austrian enable bit Note: reactive mode bit1-3, a total of three bits can be expressed 0-7, of which 0 is not used for the time being, 1-6 corresponds to the control of the six reactive modes; Note: corresponding to the corresponding reactive mode to control the corresponding function, the specifics are as follows register function descriptions; Note: Enable to set 1 for open, set 0 for close; | installer | [6 empty] | Different modes control different function registers. Each reactive mode has an enable bit, and only the corresponding reactive mode enable bit is turned on to control the function registers therein.
| 0981 | PowerFactor |  | I16 | 0.0001 |  | -10000 | 10000 | RW | Power factor, used in reactive mode one to calculate Tanphi. Positive values represent the supply of inductive under-excited reactive power, with the inverter output current overshooting the grid voltage; Negative values represent capacitive over-excitation reactive power is provided and the inverter output current lags the grid voltage; | installer
| 0982 | FixedReactivePercentage |  | I16 | 0.01 | % | -6000 | 6000 | RW | Fixed reactive power percentage for reactive mode II calculation of reactive power. Positive values represent inductive under-excitation reactive power provision, where the inverter output current overshoots the grid voltage; Negative value means capacitive over-excitation reactive power is provided and the inverter output current lags behind the grid voltage; | installer
| 0983 | ReactiveCos1 |  | I16 | 0.0001 |  | -10000 | 10000 | RW | Used for reactive mode III, first point power factor value. Positive values represent the provision of inductive under-excitation reactive power, with the inverter output current overshooting the grid voltage; Negative value means capacitive over-excitation reactive power is provided and the inverter output current lags behind the grid voltage; | installer
| 0984 | ReactivedynamicValue1 |  | I16 | 1 | % | -100 | 100 | RW | For reactive mode III, first point power percentage | installer
| 0985 | ReactiveCos2 |  | I16 | 0.0001 |  | -10000 | 10000 | RW | For reactive mode III, second point power factor value | installer
| 0986 | ReactivedynamicValue2 |  | I16 | 1 | % | -100 | 100 | RW | For reactive mode III, second point power percentage | installer
| 0987 | ReactiveCos3 |  | I16 | 0.0001 |  | -10000 | 10000 | RW | For reactive mode III, third point power factor value | installer
| 0988 | ReactivedynamicValue3 |  | I16 | 1 | % | -100 | 100 | RW | For reactive mode III, third point power percentage | installer
| 0989 | ReactiveCos4 |  | I16 | 0.0001 |  | -10000 | 10000 | RW | For reactive mode III, point 4 power factor value | installer
| 098A | ReactivedynamicValue4 |  | I16 | 1 | % | -100 | 100 | RW | For reactive mode III, fourth point power percentage | installer
| 098B | LockinV |  | U16 | 1 | % | 0 | 200 | RW | For Reactive Mode III, LockinV Voltage Value Percentage | installer
| 098C | LockoutV |  | U16 | 1 | % | 0 | 200 | RW | For reactive mode III, LockoutV voltage value percentage | installer
| 098D | HighVoltStartValue4 |  | U16 | 1 | % | 0 | 200 | RW | For reactive mode IV, percent high voltage starting voltage | installer
| 098E | HighVoltEndValue4 |  | U16 | 1 | % | 0 | 200 | RW | For reactive mode IV, high voltage termination voltage percentage | installer
| 098F | LowVoltStartValue4 |  | U16 | 1 | % | 0 | 200 | RW | For reactive mode IV, percent low voltage starting voltage | installer
| 0990 | LowVoltEndValue4 |  | U16 | 1 | % | 0 | 200 | RW | For Reactive Mode IV, LV Termination Voltage Percentage | installer
| 0991 | LockinPower4 |  | U16 | 1 | % | 0 | 100 | RW | For reactive power mode IV, Lockin power value percentage | installer
| 0992 | LockoutPower4 |  | U16 | 1 | % | 0 | 100 | RW | For reactive power mode IV, Lockout power value percentage | installer
| 0993 | MaxLeadingReactivePower4 |  | U16 | 0.01 | %Pn | 0 | 10000 | RW | For reactive mode IV, maximum percentage of excess reactive power | installer
| 0994 | ReactiveResponseWaitTime4 |  | U16 | 10 | ms | 0 | 65535 | RW | For reactive mode IV, reactive response wait time | installer
| 0995 | ReactivePowerOffset4 |  | I16 | 0.01 | %Qmax | -10000 | 10000 | RW | Used for reactive mode IV, percent reactive power offset. Offsets the reactive power curve over the entire operating voltage range. Positive values indicate overruns and negative values indicate lags. | installer
| 0996 | ReactivePowerStart4 |  | U16 | 0.01 | %Pn | -10000 | 10000 | RW | For reactive mode IV, 50% of the percentage change in reactive power range from the low voltage starting voltage to the high voltage starting voltage point. The low voltage starting voltage corresponds to the reactive power that is lagging in this register; the high voltage starting voltage corresponds to the reactive power that is ahead of this register; | installer
| 0997 | HighVoltStartValue5 |  | U16 | 1 | % | 0 | 200 | RW | For Reactive Mode V, High Voltage Starting Voltage Percentage | installer
| 0998 | HighVoltEndValue5 |  | U16 | 1 | % | 0 | 200 | RW | For reactive mode V, high voltage termination voltage percentage | installer
| 0999 | LowVoltStartValue5 |  | U16 | 1 | % | 0 | 200 | RW | For reactive mode V, percent low voltage starting voltage | installer
| 099A | LowVoltEndValue5 |  | U16 | 1 | % | 0 | 200 | RW | For Reactive Mode V, LV Termination Voltage Percentage | installer
| 099B | LockinPower5 |  | U16 | 1 | % | 0 | 100 | RW | For reactive power mode V, Lockin power value percentage | installer
| 099C | LockoutPower5 |  | U16 | 1 | % | 0 | 100 | RW | For reactive power mode V, Lockout power value percentage | installer
| 099D | MaxReactivePower5 |  | U16 | 0.01 | % | 0 | 10000 | RW | For reactive mode V, maximum reactive power percentage | installer
| 099E | ReactiveResponseWaitTime5 |  | U16 | 10 | ms | 0 | 65535 | RW | For reactive mode V, reactive response wait time | installer
| 099F | PhaseType |  | U16 |  |  | 0 | 2 | RW | For reactive power mode VI, phase type 0: Zero reactive power 1: Lagging reactive power 2: Supercharged reactive power | installer
| 09A0 | ReactiveResponsePeriod |  | U16 | 1 | unit of angle or arc equivalent one sixtieth of a degree | 1 | 65535 | RW | For reactive power (1, 2, 3, 4, 5, 6) Setting the reactive power adjustment duration | installer
| 09A1 | MaxLaggingReactivePower4 |  | U16 | 0.01 | %Pn | 0 | 10000 | RW | Reactive mode IV, maximum lagging reactive power percentage | installer
3.8 Voltage ride-through parameters (0x09C0-0x09FF)
| 09C0 | VRTConfig |  | U16 |  |  |  |  | RW | Bit0: LVRT enable bit Bit1: OVRT enable bit Bit2: zero current mode enable bit Bit3: Inherit pre-run-through reactive current Bit4: Calculate current using pre-dropout voltage Bit5: Negative sequence current enable bit Bit6: High-through active enable bitBit7: Low crossing active enable bitBit8-11: voltage ride-through current calculation mode(0: invalid; 1: Germany 4110 calculation mode, others reserved) Supplementary: 1. LVRT/OVRT/zero current mode/negative sequence current/high penetration active enable bit, the enable bit is the switch of the corresponding function, set to 1 to enable (on), set to 0 to disable (off). Note: Negative sequence current enable bit and high penetration active enable bit cannot be reflected. | installer | [6 empty] | The LVRT enable bitcontrols access to the LVRT voltage value percentage and register address (0x09C2-0x09CC) functions. The OVRTaddress (0x09CD-0x09D8) register function. Zero current mode enable bit: controls the zero current mode into low/high voltage percentage. Inheritance of reactive current before crossing controls the low/high crossing exit voltage value percentage, and the low/high crossing reactive current calculation start voltage value percentage. The functions of the corresponding registers can only be reflected if the related enable bits are turned on.
| 09C1 | LvrtInVolt |  | U16 | 1 | % | 0 | 65535 | RW | Percentage of voltage values entering the LVRT | installer | [6 empty] | 1. 0x09C0-bit0: LVRT enable bit related to Set to 1 to enable (on), set to 0 to disable (off).
| 09C2 | LvrtFirstPointVolt |  | U16 | 1 | % | 0 | 65535 | RW | Percentage of low voltage crossing first point voltage | installer
| 09C3 | LvrtFirstPointTime |  | U16 | 1 | ms | 0 | 65535 | RW | Low Voltage Crossing First Point Time | installer
| 09C4 | LvrtSecondPointVolt |  | U16 | 1 | % | 0 | 65535 | RW | Percentage of low voltage crossing second point voltage | installer
| 09C5 | LvrtSecondPointTime |  | U16 | 1 | ms | 0 | 65535 | RW | Time for low-pressure crossing of the second point | installer
| 09C6 | LvrtThirdPointVolt |  | U16 | 1 | % | 0 | 65535 | RW | Percentage of low voltage crossing third point voltage | installer
| 09C7 | LvrtThirdPointTime |  | U16 | 1 | ms | 0 | 65535 | RW | Low voltage crossing third point time | installer
| 09C8 | LvrtFourthPointVolt |  | U16 | 1 | % | 0 | 65535 | RW | Percentage of low voltage crossing point 4 voltage | installer
| 09C9 | LvrtFourthPointTime |  | U16 | 1 | ms | 0 | 65535 | RW | Time for low-pressure crossing point four | installer
| 09CA | LvrtReactiveCurrentCoefficientK |  | U16 | 0.1 | p.u. | 0 | 65535 | RW | Low-voltage ride-through reactive current coefficient K | installer
| 09CB | LvrtWaitingTimeAfterVoltageRecovery |  | U16 | 1 | ms | 0 | 65535 | RW | Waiting time after low voltage crossing restoration | installer
| 09CC | LvrtPowerBackRate |  | U16 | 1 | %Pn/min | 1 | 65535 | RW | Low-voltage ride-through power return rate | installer
| 09CD | OvrtInVlot |  | U16 | 1 | % | 0 | 65535 | RW | Percentage of voltage value entering OVRT | installer | [6 empty] | 1. 0x09C0-bit1: OVRT enable bit related to Set to 1 to enable (on), set to 0 to disable (off).
| 09CE | OvrtFirstPointVolt |  | U16 | 1 | % | 0 | 65535 | RW | Percentage of high voltage crossing first point voltage | installer
| 09CF | OvrtFirstPointTime |  | U16 | 10 | ms | 0 | 65535 | RW | High Voltage Crossing First Point Time | installer
| 09D0 | OvrtSecondPointVolt |  | U16 | 1 | % | 0 | 65535 | RW | Percentage of high voltage crossing second point voltage | installer
| 09D1 | OvrtSecondPointTime |  | U16 | 10 | ms | 0 | 65535 | RW | High Voltage Crossing Second Point Time | installer
| 09D2 | OvrtThirdPointVolt |  | U16 | 1 | % | 0 | 65535 | RW | Percentage of high voltage crossing third point voltage | installer
| 09D3 | OvrtThirdPointTime |  | U16 | 10 | ms | 0 | 65535 | RW | High Voltage Crossing Third Point Time | installer
| 09D4 | OvrtFourthPointVolt |  | U16 | 1 | % | 0 | 65535 | RW | Percentage of high voltage crossing point 4 voltage | installer
| 09D5 | OvrtFourthPointTime |  | U16 | 10 | ms | 0 | 65535 | RW | High Voltage Crossing Point 4 Time | installer
| 09D6 | OvrtReactiveCurrentCoefficientK |  | U16 | 0.1 | p.u. | 0 | 65535 | RW | High-voltage ride-through reactive current coefficient K | installer
| 09D7 | OvrtWaitingTimeAfterVoltageRecovery |  | U16 | 1 | ms | 0 | 65535 | RW | Waiting time after high voltage crossing restoration | installer
| 09D8 | OvrtPowerBackRate |  | U16 | 1 | %Pn/min | 1 | 65535 | RW | High-voltage ride-through power return rate | installer
| 09D9 | ZeroCurrentModeInLowVolt |  | U16 | 1 | % | 0 | 65535 | RW | Percentage of zero current mode into low voltage | installer
| 09DA | ZeroCurrentModeInHighVolt |  | U16 | 1 | % | 0 | 65535 | RW | Percentage of zero current mode into high voltage | installer
| 09DB | LvrtOutVolt |  | U16 | 1 | % | 0 | 65535 | RW | Percentage of LV crossing exit voltage values | installer
| 09DC | LvrtIqVoltStart |  | U16 | 1 | % | 0 | 65535 | RW | Percentage of starting voltage value for LV crossing reactive current calculation | installer
| 09DD | OvrtOutVolt |  | U16 | 1 | % | 0 | 65535 | RW | Percentage of high voltage ride-through exit voltage values | installer
| 09DE | OvrtIqVoltStart |  | U16 | 1 | % | 0 | 65535 | RW | Percentage of starting voltage value for HV ride-through reactive current calculation | installer
| 09DF | MaxUnbalanceIqPct |  | U16 | 1 | % | 0 | 65535 | RW | Percentage of maximum reactive current for unbalanced ride-through | installer
| 09E0 | OVRTActivePowerVoltMin |  | U16 | 1 | % | 0 | 65535 | RW | Percentage of starting voltage value for high penetration active power | installer
| 09E1 | LVRTActivePowerVoltMin |  | U16 | 1 | % | 0 | 65535 | RW | Percentage of starting voltage value for low penetration active power | installer
| 09E2 -- 09FF | [8 empty] | reserve
3.9 Silo, GFCI, ISO parameters (0x0A00-0x0A3F)
| 0A00 | IslandConfig |  | U16 |  |  |  |  | RW | Bit0: Islanding Enable Register Bit1: Single-phase islanding enable (for three-phase inverters) | installer | [6 empty] | Insulation impedance enable register:controls the insulation impedance protection value and the component leakage current limit to ground, the product of the values of these two registers is a set fixed value; GFCI enable register:a switch for the leakage current limit (not open for the time being, the setup is invalid), but the leakage current limit register can not be written to the value, the program is written dead;
| 0A01 | GFCIConfig |  | U16 |  |  |  |  | RW | Bit0: GFCI enable register | installer
| 0A02 | ISOConfig |  | U16 |  |  |  |  | RW | Bit0: Insulation impedance enable register Bit1: Ground detection enable register | installer
| 0A03 | InsulationProtectionValue |  | U16 | 1 | kΩ | 30 | 65535 | RW | Insulation impedance protection value | installer
| 0A04 | IsoLeakageCurrentLimit |  | U16 | 1 | mA | 1 | 50 | RW | Component leakage current limit to ground | installer
| 0A05 | GFCILimit |  | U16 | 1 | mA/kVA | 1 | 50 | RW | Leakage current limit (not open yet, setting is invalid) | installer
| 0A06 | PE_N_Config |  | U16 |  |  |  |  | RW | PE and N control registers Bit0: Off-grid PEN short enable bit Bit1: N line detection enable bit | installer
| 0A07 | IslandDetectSensitivity |  | U16 |  |  |  |  | RW | Silo detection sensitivity | installer
| 0A08 | PEProtectionValue |  | U16 | 1 | kΩ | 1000 | 65535 | RW | Ground fault judgment threshold | installer
| 0A09 | SpecialCertification |  | U16 |  |  |  |  | RW | Bit0:Calculate active and reactive power by battery power | installer
| 0A0A -- 0A3F | [8 empty] | reserve
3.10 Pull Arc (0x0A40-0x0A7F)
| 0A40 -- 0A7F | [8 empty] | reserve
IV. Parameter setting area (0x1000-0x17FF)
4.1 Basic Parameter Configuration (0x1000-0x10FF) |  |  | Time setting, communication parameter setting, language, battery parameter setting, etc.
| 1000 -- 1003 | AddressMask_Config_Basic1 |  | U64 |  |  |  |  | R | Mask area for the 64 register address words starting at this address. Refer to the description of address 0x0040 | end user | 0 | 0000000F |  |  |  |  | Used to distinguish which addresses are valid and which are invalid, the main function is that different models use different registers, through the mask to do the distinction. This area supports arbitrary reading.
System Time 2-2 | 1004 | SysTimeConfig_Year |  | U16 |  | surname Nian | 0 | 99 | RW | System time - year; Actual year equals 2000 + register value | end user | [6 empty] | When writing, the fixed first address is 0x1004 and the length is 7. The write data is saved in the EEPORM.
| 1005 | SysTimeConfig_Month |  | U16 |  | moon | 1 | 12 | RW | System time - month | end user
| 1006 | SysTimeConfig_Date |  | U16 |  | date | 1 | 31 | RW | System time - day minutes | end user
| 1007 | SysTimeConfig_Hour |  | U16 |  | hour | 0 | 23 | RW | System time - hours | end user
| 1008 | SysTimeConfig_Minute |  | U16 |  | ingredient | 0 | 59 | RW | System time-minutes | end user
| 1009 | SysTimeConfig_Second |  | U16 |  | unit of angle or arc equivalent one sixtieth of a degree | 0 | 59 | RW | System Time-Second | end user
| 100A | SysTimeConfig_Control |  | U16 |  |  | 1 | 1 | RW | When the write value is 1, the value in the system time shadow register is updated to the actual system time; On read, the status of the last write operation is returned: 0x0000: Success 0x0001: operation in progress 0xFFFB: operation failed, the controller refuses to respond (maybe the controller is busy or misconfigured) 0xFFFC: operation failed, controller no answer 0xFFFD: operation failed, current function is disabled 0xFFFE: operation failed, parameter access failed 0xFFFF: operation failed, input parameter is wrong | end user
RS485 Parameter Setting | 100B | RS485Config_Address |  | U16 |  |  | 1 | 247 | RW | RS485 Configuration-Address | end user | [6 empty] | When writing, the fixed first address is 0x100B and the length is 5.
| 100C | RS485Config_Baud |  | U16 |  |  | 0 | 4 | RW | RS485 baud rate selection; 0: 4800bps 1: 9600bps (default) 2: 19200bps 3: 38400bps 4: 57600bps 5: 115200bps 10: 1200bps 11: 2400bps | end user
| 100D | RS485Config_StopBit |  | U16 |  |  | 0 | 2 | RW | RS485 stop bit selection; 0: 1 bit stop bit (default) 1: 1.5-bit stop bit 2: 2-bit stop bit | end user
| 100E | RS485Config_ParityBit |  | U16 |  |  | 0 | 4 | RW | RS485 parity bit selection; 0: No checksum/None (default) 1: Even parity/Even 2: Odd parity/Odd 3: High/Mark 4: Low/Space | end user
| 100F | RS485Config_Control |  | U16 |  |  | 1 | 1 | RW | When the write value is 1, the value in the RS485 configuration shadow register is updated to the system RS485 configuration; When reading, the status of the last write operation is returned: 0x0000: Success 0x0001: operation in progress 0xFFFB: operation failed, the controller refuses to respond (maybe the controller is busy or misconfigured) 0xFFFC: operation failed, controller no answer 0xFFFD: operation failed, current function is disabled 0xFFFE: operation failed, parameter access failed 0xFFFF: operation failed, input parameter is wrong | end user
PV input mode setting | 1010 | PV_InputMode_Config |  | U16 |  |  | 0 | 1 | RW | PV input mode selection; 0: Parallel mode 1: Independent mode (default) | installer | [6 empty] | When writing, this address is a fixed first address with a length of 1. This setting and the following input channel type selection will only be available one on a model.
| 1011 -- 1020 | InputType_Channel0_Config -- InputType_Channel15_Config |  | U16 |  |  | 0 | 255 | RW | Input channel 0-15 type selection (16); Value 0 indicates that the current channel is not in use; Values 1 to 127 indicate that the current channel is a photovoltaic panel input; Values 128 to 255 indicate that the current channel is a battery input; If the values of two or more channels are the same and greater than zero, it means that these channels are input in parallel; | installer | [6 empty] | When writing, the fixed first address is 0x1011, and the length is any value from 1 to 17. The input channel is different for different models, so you can choose it according to the actual input channel. And the modification of the input channel should be done when the inverter is not in grid-connected or off-grid state.
| 1021 | InputType_Control |  | U16 |  |  | 1 | 1 | RW | When the write value is 1, the value in the input channel type shadow register is updated to the system input channel type configuration; On read, the status of the last write operation is returned: 0x0000: Success 0x0001: operation in progress 0xFFFB: operation failed, the controller refuses to respond (maybe the controller is busy or misconfigured) 0xFFFC: operation failed, controller no answer 0xFFFD: operation failed, current function is disabled 0xFFFE: operation failed, parameter access failed 0xFFFF: operation failed, input parameter is wrong | installer
Remove the safety parameters from the USB flash drive | 1022 | SafetyUpdateFromUSB_Control |  | U16 |  |  | 1 | 1 | RW | A write value of 1 is used for the communication board to remove the safety parameters from the USB flash drive; When reading, it returns the status of the last write operation: 0x0000: Success 0x0001: operation in progress 0xFFFB: operation failed, the controller refuses to respond (maybe the controller is busy or misconfigured) 0xFFFC: operation failed, controller no answer 0xFFFD: operation failed, current function is disabled 0xFFFE: operation failed, parameter access failed 0xFFFF: operation failed, input parameter is wrong | installer | [6 empty] | Write is not yet available, only read is supported.
anti-streaming | 1023 | AntiReflux_Control |  | U16 |  |  | 0 | 2 | RW | Anti-reverse flow enable control 0: Disable anti-reverse flow function 1: Default anti-reverse current mode 2: Three-phase average power anti-reverse current mode 3: Phase power mode4: Master-slave anti-reverse current mode (coordinated anti-reverse current under multiple parallel machines) | installer | [6 empty] | When writing, the fixed first address is 0x1023 and the length is 2
| 1024 | AntiReflux_Power |  | U16 | 100 | W | 0 | 65535 | RW | Anti-backflow power | installer
IV Curve Scan Settings | 1025 | IVCurveScan_Control |  | U16 |  |  | 0 | 1 | RW | IV Curve Scan Enable Control | installer | [6 empty] | When writing, the fixed first address is 0x1025 and the length is 2
| 1026 | IVCurveScan_Period |  | U16 | 1 | minutes | 5 | 65535 | RW | IV curve scanning cycle | installer
| 1027 | IVCurveScan_Oneshot |  | U16 |  |  | 1 | 1 | RW | IV curve scan activation; When the write value is 1, 1 IV curve scan is activated; On read, return to the status of the last write operation: 0x0000: Success 0x0001: operation in progress 0xFFFB: operation failed, controller refuses to respond (maybe the controller is busy or misconfigured) 0xFFFC: operation failed, controller no answer 0xFFFD: operation failed, current function is disabled 0xFFFE: operation failed, parameter access failed 0xFFFF: operation failed, input parameter is wrong | installer | [6 empty] | When writing, the fixed first address is 0x1027 and the length is 1
| 1028 | IVCurveScan_ReadChannel |  | U16 |  |  | 0 | 31 | RW | IV curve scan return data channel. This register is used to specify the PV channel corresponding to the IV curve scan result return value. | installer | [6 empty] | When writing, the fixed first address is 0x1028, the length is 1, and the write value cannot exceed the maximum PV channel of the inverter
Emergency power supply | 1029 | EPS_Control |  | U16 |  |  | 0 | 2 | RW | Emergency power enable control 0: Disable emergency power supply (default) 1：Enable emergency power supply, disable cold start 2：Enable cold start by turning on the emergency power supply. | end user | [6 empty] | When writing, the fixed first address is 0x1029 and the length is 2
| 102A | EPS_WaitTime |  | U16 | 1 | unit of angle or arc equivalent one sixtieth of a degree | 0 | 65535 | RW | Waiting time for emergency power supply activation (reserved function) | end user
Battery activation | 102B | BatteryActive_Control |  | U16 |  |  | 0 | 1 | RW | Battery auto-activation enable control | end user | [6 empty] | When writing, the fixed first address is 0x102b and the length is 2
| 102C | BatteryActive_Oneshot |  | U16 |  |  | 1 | 1 | RW | Battery activation; When the write value is 1, 1 battery activation is performed; On read, return to the status of the last write operation: 0x0000: Success 0x0001: operation in progress 0xFFFB: operation failed, controller refuses to respond (maybe the controller is busy or misconfigured) 0xFFFC: operation failed, controller no answer 0xFFFD: operation failed, current function is disabled 0xFFFE: operation failed, parameter storage failed 0xFFFF: operation failed, input parameter is wrong | end user
Automatic CT calibration | 102D | CT_Auto_Calibrate |  | U16 |  |  | 1 | 1 | RW | CT auto-calibration; When the write value is 1, 1 CT auto-correction is performed; When reading, return to the status of the last write operation: 0x0000: Success 0x0001: operation in progress 0xFFFB: operation failed, the controller refuses to respond (maybe the controller is busy or misconfigured) 0xFFFC: operation failed, controller no answer 0xFFFD: operation failed, current function is disabled 0xFFFE: operation failed, parameter storage failed 0xFFFF: operation failed, input parameter is wrong | installer | [6 empty] | When writing, the fixed first address is 0x102D and the length is 1
Automated testing in Italy | 102E | Italy_AutoTest |  | U16 |  |  | 1 | 2 | RW | Automated Testing in Italy Write: 0x0001: execution of standard test (S); 0x0002: perform fast test (F); On read, returns the status of the last write operation: 0x0000: success 0x0001: operating standard test 0x0002: operating fast test 0xFFFB: operation failed, controller refuses to respond (maybe the controller is busy or misconfigured) 0xFFFC: operation failed, controller no answer 0xFFFD: operation failed, current function is disabled 0xFFFE: operation failed, parameter storage failed 0xFFFF: operation failed, input parameter is wrong | installer | [6 empty] | When writing, the fixed first address is 0x102E and the length is 1
Heating Membrane Enabling | 102F | Heating_Film_en |  | U16 | 1 |  |  |  | RW | Heating membrane enable: 0: disable 0: disabled 1: Enable | installer
Power statistics backhaul | 1030 | EnergyStatistics_Date_Year |  | U16 | 1 | surname Nian | 0 | 19 | RW | Electric energy statistics return date setting register. This register specifies the year of the returned electrical energy data. The year refers to the most recent Nth year relative to the inverter system time. n is the register value. 0: the current year of the system time; 1: 1 year before system time; ... 19: 19 years before system time. | installer | [6 empty] | These four registers need to be used together to read the current or previous power data. The read data is stored in the address 0x1610 to 0x165F area. When writing, the fixed first address is 0x1030 and the length is 4
| 1031 | EnergyStatistics_Date_Month |  | U16 | 1 | moon | 1 | 12 | RW | Electric energy statistics return date setting register. This register specifies the month in which the returned electrical energy data will be returned. | installer
| 1032 | EnergyStatistics_Date_Date |  | U16 | 1 | date | 1 | 31 | RW | Electric energy statistics return date setting register. This register specifies the day and minute of the returned electrical energy data. | installer
| 1033 | EnergyStatistics_Config |  | U16 |  |  |  |  | RW | Power statistics return setting register. High byte: date and time setting for the return data. 0x01: Daily, the first 24 data in the return area are valid; 0x02: Monthly, the first 31 data in the return area are valid; 0x03: yearly, the first 12 data in the return area are valid; 0x04: life cycle, the first 20 data in the return area are valid; Other: invalid. Low byte: physical quantity setting for the return data. 0x01: PV power generation; 0x02: load power consumption; 0x03: system buy power quantity; 0x04: amount of power sold by the system; 0x05: battery charging quantity; 0x06: battery discharge amount; Others: invalid. | installer
multilingualism | 1034 | Language |  | U16 |  |  | 0 | 65535 | RW | Inverter menu language number setting register. 0: Chinese 1: English 2: Italian 3: German 4: French 5: Portuguese 6: Ukrainian 7: Slovak 8: Spanish 9: Finnish 10: Polish 11: Korean 12: Japanese 13: Russian 14: Czech | end user | [6 empty] | When writing, the fixed first address is 0x1034 and the length is 1
parallel control | 1035 | Parallel_Control |  | U16 |  |  | 0 | 2 | RW | 0: Disable parallel function 1: Enable AC parallel function 2: Enable AC+BAT parallel function | installer | [6 empty] | When writing, the fixed first address is 0x1035 and the length is 3. The parallel function may be different for different models, so set it according to the actual model.
| 1036 | Parallel_Master_Slave |  | U16 |  |  | 0 | 1 | RW | 0: This machine is configured as a slave 1: This machine is configured as a master (default) | installer
| 1037 | Parallel_Address |  | U16 |  |  | 0 | 10 | RW | Local parallel address | installer
3-phase 4-wire mode grid unbalance support control | 1038 | UnbalancedSupport_Control |  | U16 |  |  | 0 | 1 | RW | 3-phase 4-wire mode grid unbalance support control registers 0: Disable unbalance support function (default) 1: Enable unbalance support function | installer | [6 empty] | When writing, the fixed first address is 0x1038 and the length is 1
Power multiplier | 1039 | PV_Generation_Ratio |  | U16 | 0.001 | p.u. | 800 | 3600 | RW | Power generation multiplier. Default value 1000 | installer | [6 empty] | Not used yet, can be read, but data is meaningless
| 103A | Energy_Purchase_Ratio |  | U16 | 0.001 | p.u. | 800 | 1500 | RW | Buy the power multiplier. Default value 1000 | installer
| 103B | Energy_Selling_Ratio |  | U16 | 0.001 | p.u. | 800 | 1500 | RW | Sell the power multiplier. Default value 1000 | installer
| 103C | Bat_Charge_Ratio |  | U16 | 0.001 | p.u. | 800 | 1500 | RW | Charge volume multiplier. Default value 1000 | installer
| 103D | Bat_Discharge_Ratio |  | U16 | 0.001 | p.u. | 800 | 1500 | RW | Discharge volume multiplier. Default value 1000 | installer
logical interface control | 103E | LogicInterface_Control |  | U16 |  |  | 0 | 1 | RW | Logical Interface Control Register 0: Disable 1: Enable | installer | [6 empty] | When writing, the fixed first address is 0x103E and the length is 1
logical interface value | 103F | LogicInterface_Value |  | U16 | 1 |  | 0 | 127 | R | Logical interface value 0: no logical interface enable enabled or enable logical interface 0 1-8: corresponds to logical interfaces DRMS 1-8; 127: indicates that logical interfaces 1-8 are enabled, but the value is invalid | installer | [6 empty] | Readable, the user sees if the user has external access to the logical interface.
| 1040 -- 1043 | AddressMask_Config_Basic2 |  | U64 |  |  |  |  | R | Mask area for the 64 register address words starting at this address. Refer to the description of address 0x0040 | end user | 0 | 0000000F |  |  |  |  | Used to distinguish which addresses are valid and which are invalid, the main function is that different models use different registers, through the mask to do the distinction. This area supports arbitrary reading.
Battery Parameter Configuration | 1044 | BatConfig_ID |  | U16 |  |  | 0 | 7 | RW | Battery serial number. The serial number specified in this register corresponds to the actual battery input connector of the inverter. Upon successful write to this register, the battery parameters will be updated to the parameters corresponding to the serial number written. | end user | [6 empty] | When the battery is not a lead-acid battery, the default parameters for lead-acid batteries are meaningless. The parameters of different battery types have different limitations and some parameters cannot be modified, so the default values are used, please refer to the battery documentation for details. When writing, the fixed first address is 0x1044, and the length is any value from 1 to 23.
| 1045 | BatConfig_Address |  | U16 |  |  | 0 | 99 | RW | Battery Address. If multiple batteries are allowed to be accessed in the system, this register is used to mark the battery address of the physical interface that corresponds to the battery serial number. | end user
| 1046 | BatConfig_Potocol |  | U16 |  |  | 0 | 65535 | RW | Battery Parameters-Communication Protocol 0: Shouhang built-in BMS/DEFAULT 1：PYLON protocol/PYLON 2：Shouhang protocol / GENERAL 3：AMASS 4：LG 5：Alpha. 6：CATL 7: Weco 8：Fronus 9：EMS 10: Nilar 11：BTS 5K 12：Motion for | end user
| 1047 | BatConfig_Voltage_Over |  | U16 | 0.1 | V | 0 | 65535 | RW | Battery parameters - Overvoltage protection value | installer
| 1048 | BatConfig_Voltage_Charge |  | U16 | 0.1 | V | 0 | 65535 | RW | Battery Parameters-Charge Voltage | installer
| 1049 | BatConfig_Voltage_Lack |  | U16 | 0.1 | V | 0 | 65535 | RW | Battery Parameters - Undervoltage Protection Voltage Lead-acid battery visible | installer
| 104A | BatConfig_Voltage_Discharge_Stop |  | U16 | 0.1 | V | 0 | 65535 | RW | Battery Parameters-Minimum Discharge Voltage | installer
| 104B | BatConfig_Current_Charge_Limit |  | U16 | 0.01 | A | 0 | 65535 | RW | Battery Parameters - Maximum Charge Current Limit | end user
| 104C | BatConfig_Current_Discharge_Limit |  | U16 | 0.01 | A | 0 | 65535 | RW | Battery parameters - Maximum discharge current limit | end user
| 104D | BatConfig_Depth_of_Discharge |  | U16 | 1 | % | 1 | 90 | RW | DOD indicates the maximum discharge when the grid is normal, when SOC&lt;1-DOD the inverter stops discharging, the inverter will also stop discharging based on other conditions; DOD&lt;=EOD | end user
| 104E | BatConfig_End_of_Discharge |  | U16 | 1 | % | 1 | 90 | RW | EOD indicates the maximum off-grid discharge, when SOC&lt;1-EOD the inverter stops discharging, the inverter will also stop discharging according to other conditions. | end user
| 104F | BatConfig_Capacity |  | U16 | 1 | Ah | 1 | 65535 | RW | Battery parameters - battery capacity (default 50) | end user
| 1050 | BatConfig_Voltage_Nominal |  | U16 | 0.1 | V | 0 | 65535 | RW | Battery Parameters - Rated Battery Voltage (default 0) | end user
| 1051 | BatConfig_Cell_Type |  | U16 | 1 |  | 0 | 6 | RW | Battery Parameters - Cell Type; 0: lead acid (customized) 1: lithium iron phosphate 2: ternary 3: lithium titanate 4: AGM 5: Gel 6：Flooded | end user
| 1052 | BatConfig_EPS_Buffer |  | U16 | 1 | % | 5 | 100 | RW | Battery Parameters - Off-grid recovery discharge hysteresis; EPS_Buffer is not greater than EOD | end user
| 1053 | BatConfig_Control |  | U16 |  |  |  |  | RW | Battery parameter write control; With a write value of 1, the value in the battery parameter shadow register is updated to the system battery parameter configuration; For a write value of 2, the value in the battery parameter shadow register is updated to the default value of BatConfig_Potocol; On read, the status of the last write operation is returned: 0x0000: Success 0x0001: operation in progress 0xFFFB: operation failed, controller refuses to respond (maybe the controller is busy or misconfigured) 0xFFFC: operation failed, controller no answer 0xFFFD: operation failed, current function is disabled 0xFFFE: operation failed, parameter storage failed 0xFFFF: operation failed, input parameter is wrong | end user
| 1054 | BatConfig_Address2 |  | U16 |  |  | 0 | 99 | RW | Battery Address 2. If multiple batteries are allowed to be accessed in the system, this register is used to mark the battery address of the physical interface that corresponds to the battery serial number. | end user
| 1055 | BatConfig_Address3 |  | U16 |  |  | 0 | 99 | RW | Battery Address 3. If multiple batteries are allowed to be accessed in the system, this register is used to mark the battery address of the physical interface that corresponds to the battery serial number. | end user
| 1056 | BatConfig_Address4 |  | U16 |  |  | 0 | 99 | RW | Battery Address 4. If multiple batteries are allowed to be accessed in the system, this register is used to mark the battery address of the physical interface that corresponds to the battery serial number. | end user
| 1057 | BatConfig_TEMPCO |  | I16 | 0.1 | mV/Cell | -60 | 0 | RW | Battery Parameters - Temperature compensation factor for lead-acid batteries. | end user
| 1058 | BatConfig_Voltage_Recovery_Buffer |  | U16 | 0.1 | V |  |  | RW | Battery Parameters - Lead-acid battery recovery discharge voltage increment. For example: "Battery voltage <最低放电电压”时停止放电； “电池电压>minimum discharge voltage + resuming discharge voltage increment" when resuming discharge. | end user
| 1059 | BatConfig_Control_Bits |  | U16 |  |  |  |  | RW | Battery Parameter-Function Control Bit Bit0: SOC control disabled (0: use SOC; 1: disable SOC) | end user
| 105A | BatConfig_Voltage_Float |  | U16 | 0.1 | V |  |  | RW | Battery Parameters-Lead Acid Battery Float Voltage
| 105B - 105F | [8 empty] | reserve
PCC Power Harvesting Device Configuration | 1060 | PCCSampleMode |  | U16 |  |  | 0 | 2 | RW | PCC Power Harvesting Device Configuration 0: Not used 1: Power meter 2: CT 3: ARPC 4: Collector | end user
Resonance Detection Sensitivity | 1061 | Resonance_Sensitivity |  | U16 |  |  | 1 | 100 | RW | Resonance Detection Sensitivity | end user
CT ratio setting | 1062 | CT_rate |  | U16 |  |  |  |  | RW | CT ratio setting | [7 empty] | When writing, the fixed first address is 0x1062 and the length is 1
Hard anti-reverse flow switches | 1063 | Hard_Reflux_Config |  | U16 |  |  |  |  | RW | Hard anti-reverse flow switch: 0 disable/1 use | [7 empty] | Not used (only for three-phase energy storage models)
Wet/dry contact control | 1064 | Dry_Contact |  | U16 |  |  | 0 | 3 | RW | Dry contact control 0: Disable dry contact; 1: generator mode; 2: Relay mode 1 (off-grid output high, rest low); 3: Relay mode 2 (off-grid output low, rest high); | [7 empty] | When writing, the fixed first address is 0x1064 and the length is 1
| 1065 | Wet_Contact |  | U16 |  |  | 0 |  | RW | Wet contact control (reserved) 0: Wet contact disabled | [7 empty] | Not yet used, can be read
PV branch | 1066 | pv_branch_current_limit |  | U16 | 0.1 | A | 0 | 65535 | RW | PV branch circuit overcurrent protection
Grid detection and control | 1067 | Grid_Detect_Control |  | U16 |  |  | 0 | 65535 | RW | Grid-side detection control, coded by bit, set to 1 to take effect: bit0-Missing phase detection enable; Other reserved.
Out-of-phase detection field value | 1068 | LostPhase_Detect_Threshold |  | U16 | 0.1 | % | 0 | 1000 | RW | voltage field value
PCC bias power | 1069 | PCCPowerDeviation |  | I16 | 1 | W | -300 | 300 | RW | PCC Acquisition Power Deviation Calibration (Total Power)
Buy electric power control | 106A | PCCInputPowerControl |  | U16 |  |  | 0 | 1 | RW | Buy power power limit enable control (total power): 0: Disable buyer power limit function 1: Enable buyer power limit function | installer | [6 empty] | Fixed first address on write is 0X106A. length is 2
| 106B | PCCInputLimitPower |  | U16 | 100 | W | 0 | 65535 | RW | Purchased power limit power (total power) | installer
Intelligent Load Control | 106C | SmartLoadMode |  | U16 | 1 |  | 0 | 3 | RW | Smart Load Mode Selection 0: Smart Load off 1: Enable Smart Load 2: Timing Mode 3: Intelligent Mode Mode) | installer | [6 empty] | When writing parameters via modbus, the starting address should be 0x106C, and the writing length should be 1 or 4. When the writing length is 1, only the intelligent load mode can be set, and when the writing length is 4, the register values of the corresponding addresses need to be set in turn; the register at the 0x106F address turns on the power for the time being without use, and the value 0 can be written;
| 106D | SmartLoadStartTime |  | U16 | 1 | Hours minutes | 0 | 23:59 | RW | High byte: startup time hours Low byte: startup time in minutes Note: The time defaults to 0 hours and 0 minutes. | installer
| 106E | SmartLoadStopTime |  | U16 | 1 | Hours minutes | 0 | 23:59 | RW | High byte: end time hours Low byte: end time minutes Note: The time defaults to 0 hours and 0 minutes. | installer
| 106F | SmartLoadTrunOnPower |  | U16 | 0.1 | W | 0 | 65535 | RW | Intelligent load turn-on power
Number of parallel machines | 1070 | ParallelModuleNum |  | U16 | 1 |  | 1 | 65535 | RW | Number of parallel machines | installer
DRM shutdown control | 1071 | DRMShutdownControl |  | U16 | 1 |  |  |  | RW | Bit0: DRM0 control (0:DRM0 on, 1:DRM0 off) Bit1~Bit15:Reserved Note: Set 1 for off, set 0 for on | installer
| 1072 - 107F | [8 empty] | reserve
| 1080 -- 1083 | AddressMask_Config_Basic3 |  | U64 |  |  |  |  | R | Mask area for the 64 register address words starting at this address. Refer to the description of address 0x0040 | installer | 0 | 0000000F |  |  |  |  | Used to distinguish which addresses are valid and which are invalid, the main function is that different models use different registers, through the mask to do the distinction. This area supports arbitrary reading.
Arc Detection Parameter Configuration | 1084 | ArcingAlarmEnable |  | U16 |  |  | 1 |  | RW | Enable Arc Detection | installer | [6 empty] | Not yet used, can be read
| 1085 | PeakToPeakSet |  | U16 | 1 |  | 0x64 |  | RW | Peak value setting | installer
| 1086 | VarianceSet |  | U16 | 1 |  | 0x95 |  | RW | Variance setting | installer
| 1087 | HarmonicEnergySet |  | U16 | 1 |  | 0x01 |  | RW | Harmonic energy setting | installer
| 1088 | AmplitudeVarianceSet |  | U16 | 1 |  | 0x01 |  | RW | Amplitude Variance Setting | installer
| 1089 | TimeDomWeiSet |  | U16 | 1 |  | 0x01 |  | RW | Time domain weight setting | installer
| 108A | FreDomWeiSet |  | U16 | 1 |  | 0x05 |  | RW | Frequency domain weight setting | installer
| 108B | ArcDetectSensitivity |  | U16 | 1 |  | 0x14 |  | RW | Arc detection sensitivity | installer
| 108C | ArcAlarmShutdownThreshold |  | U16 | 1 |  | 0x05 |  | RW | Arc Alarm Count Shutdown Threshold | installer
| 108D | ArcSelfCheckCommand |  | U16 |  |  | 0x01 |  | RW | Write 1 to start self-test (self-test all channels). It is automatically cleared after the self-test. | installer
| 108E | ArcingAlarmClear |  | U16 | 1 |  | 0x1234 | 0x1234 | RW | Write 0x1234 Clear Arc Alarm (all channels) | installer
| 108F | ArcAlarmCnt |  | U16 | 1 |  |  |  | RW | Arc Alarm Counting
| 1090 | AfciResult |  | U16 | 1 |  |  |  | R | Handshake results
| 1091 | SelfCheckResult |  | U16 |  |  |  |  | R | Bit0-Channel 1 self-test result (0 self-test success; 1 self-test failure or no self-test) Bit1-channel 2,Bit2-channel 3,Bit3-channel 4,Bit4-channel 5,Bit5-channel 6,
| 1092 | SelfCheckState |  | U16 |  |  |  |  | R | Channel self-test status 0: No self-test 1：Self-test in progress 2：Self-test completed
| 1093 - 109F | [8 empty] | reserve
PLC Configuration | 10A0 | PLC_Enable_Setting |  | U16 |  |  |  |  | RW | PLC sets the run bit, 0 is not allowed, 1 is allowed | [7 empty] | Not yet used, can be read
| 10A1 | PLC_Com_Property |  | U16 | NULL | NULL | 0 |  | RW | bit0-bit1:0~1 corresponds to 1/1.5 bit2~bit4:0~7 corresponds to NONE/odd/EVEN three kinds of checksum bit5~bit7 0~3 corresponds to 8/9l two kinds of data bit length bit8~15 0~7 corresponds to 4800/9600/19200/38400/115200 | end user
| 10A2 -- 10A4 | [8 empty] | reserve
Bluetooth Configuration | 10A5 | BLE_Enable_Setting |  | U16 | NULL | NULL | 0 | 1 | RW | BLE Bluetooth set run bit, 0 not allowed, 1 allowed | [7 empty] | When writing, the fixed first address is 0x10A5 and the length is 1
| 10A6 | BLE_Com_Property |  | U16 | NULL | NULL | 0 | 65535 | RW | bit0-bot1:0~1 corresponds to 1/1.5 bit2~bit4:0~7 corresponds to NONE/odd/EVEN three kinds of check mode bit5~bit7 0~1 corresponds to 8/9l data bit lengths. bit8~15 0~7 correspond to 4800/9600/19200/38400/115200 | [7 empty] | Not yet used, can be read
| 10A7 - 10AF | [8 empty] | reserve
PID Parameter Configuration | 10B0 | PID_Auto_running_enable |  | U16 |  |  | 0 | 1 | RW | PID start auto run. 0 means disabled; 1 means enabled. | end user | [6 empty] | Not yet used, can be read
| 10B1 | PID_Working_Start_Time |  | BCD16 | 1 | Minute | 0 | 2359 | RW | PID operating start time (BCD code). For example, the minimum value 0x0000 indicates 00:00; The maximum value 0x2359 indicates 23:59. | end user
| 10B2 | PID_Working_Hours |  | U16 | 1 | Minute | 0 | 65535 | RW | PID operating hours. | end user
| 10B3 | PID_Working_PV_Threshold |  | U16 | 0.1 | V | 0 | 65535 | RW | PID startup PV value threshold. PID startup is allowed only when the PV voltage is below the threshold. | end user
| 10B4 | PID_Break_Restart_Delay |  | U16 | 1 | Minute | 0 | 65535 | RW | Reboot wait time after PID fault shutdown. | end user
Remote control and display of CLS status | 10B5 | CLSAntiRefluxState |  | U16 |  |  | 0 | 3 | R | CLS anti-reverse flow status 0-Normal state; 1-Critical state; 2-Low power state; 3-fault state | installer
| 10B6 | CLSRemoteControl |  | U16 |  |  | 0 | 65535 | RW | Bit0--CLS lock status clearing Bit1 - CLS status reset | installer
Device Password Reset Command | 10B7 | PasswordResetCommand |  | U16 |  |  | 0 | 65535 | W | Password reset control: 1: Reset Password Other: Invalid | end user | [6 empty] | Supports UK and Ireland national safety regulations only | 3PH,ESI,EP
| 10B8 | [8 empty] | reserve
Generator parameter configuration items | 10B8 | Generator_Mode_Setting |  | U16 | 1 |  | 0 |  | RW | Generator control Bit0--control mode (0:manual mode, 1:automatic mode) Bit1--Manual control (0:manual off, 1:manual on) Bit2 - generator lockout (0:disable, 1:enable)
| 10BA | off_arid_dq_power |  | U16 | 0.1 | KW | 0.1 | 65535 | RW | peak power
| 10BB | generator_start_voltage |  | U16 | 0.1 | V |  | 65535 | RW | starting voltage
| 10BC | generator_stop_voltage |  | U16 | 0.1 | V |  | 65535 | RW | Stop Voltage
| 10BD | generator_soc |  | U16 | 1 | % | 0 | 65535 | RW | High byte: start SOC Low byte: stop SOC
| 10BE - 10BF | [8 empty] | reserve
Anti-backflow communication configuration | 10C0 | AntiRefluxComm_ProtectionControl |  | U16 |  |  |  |  | RW | Reverse current communication protection enable bit0: Disable1Enable
| 10C1 | AntiRefluxComm_ProtectionTime |  | U16 |  | unit of angle or arc equivalent one sixtieth of a degree | 0 | 65535 | RW | Backflow communication protection time
| 10C2 - 10C3 | [8 empty] | reserve
4.2 Remote Control (0x1100-0x12FF) |  |  | Controls such as remote power-up and operating mode parameters
| 1100 -- 1103 | AddressMask_Config_Remote1 |  | U64 |  |  |  |  | R | Mask area for the 64 register address words starting at this address. Refer to the description of address 0x0040 | end user | 0 | 0000000F |  |  |  |  | Used to distinguish which addresses are valid and which are invalid, the main function is that different models use different registers, through the mask to do the distinction. This area supports arbitrary reading.
Remote switch on/off | 1104 | Remote_On_Off_Control |  | U16 |  |  | 0 | 1 | RW | Remote power on/off. 0x0000: power off 0x0001: Power on | end user | [6 empty] | When writing, the fixed first address is 0x10A5 and the length is 1
power control | 1105 | Power_Control |  | U16 |  |  |  |  | RWV | Power control; Bit0: active enable bit Bit1: reactive power enable bit Bit2: reactive mode selection bit (0: Reactive_Power; 1: Power_Factor) Bit3: SVG enable bit Bit4: SVG reactive power mode selection bit (0: Fixed_Reactive_Power; 1: Reactive_Power) Bit5: SVG power factor compensation enable bit Bit6~Bit7: reserved Bit8: Night operation enable bit Note: Setting 1 is enable, setting 0 is disable. | end user | [6 empty] | When writing, the fixed first address is any address in this range and the length is the length of the range
| 1106 | Active_Power_Export_Limit |  | U16 | 0.1 | % | 0 | 1000 | RWV | Percentage of maximum active power output | end user
| 1107 | Active_Power_Import_Limit |  | U16 | 0.1 | % | 0 | 1000 | RWV | Percentage of maximum active power input | end user
| 1108 | Reactive_Power_Setting |  | I16 | 0.1 | % | -1000 | 1000 | RWV | Reactive power percentage. Note: Maximum reactive power is limited by the specific model. | end user
| 1109 | Power_Factor_Setting |  | I16 | 0.01 | p.u. | -100 | 100 | RWV | Power Factor. Note: The minimum power factor is limited by the specific model. | end user
| 110A | Active_Power_Limit_Speed |  | U16 | 1 | % | 1 | 65535 | RWV | Rate of change of active power limit | end user
| 110B | Reactive_Power_Response_Time |  | U16 | 0.1 | second | 0 | 65535 | RWV | Reactive power setting response time | end user
| 110C | SVG_Fixed_Reactive_Power_Setting |  | I16 | 0.1 | kVar | -32768 | 32767 | RWV | Fixed reactive power magnitude in SVG mode | end user | [6 empty] | Not yet used, can be read
| 110D | Reactive_Power_Adjust_Limit |  | I16 | 0.1 | kVar | -32768 | 32767 | RWV | SVG Power Factor Compensation Reactive Power Regulation | end user
| 110E - 110F | [8 empty] | reserve
Energy storage operating mode setting | 1110 | Energy_Storage_Mode_Control |  | U16 |  |  | 0 | 4 | RW | Energy storage operating mode setting; 0: self-generation and self-consumption mode 1: time-sharing tariff mode 2: Timed charging and discharging mode 3: Passive mode 4: Peak shaving mode 5: Off-grid mode 6: Generator mode Used to change the operating mode. | end user | [6 empty] | When writing, the fixed first address is 0x1110 and the length is 1
timed charging and discharging | 1111 | Timing_ID |  | U16 |  |  | 0 | 3 | RW | Timed charging and discharging-rule serial number; The smaller the serial number, the higher the priority. Upon successful write to this register, the Timed Charge and Discharge parameter will be updated to the parameter corresponding to the serial number written. | end user | [6 empty] | When writing, the fixed first address is 0x1111 and the length is 1 or 15 When the length is 1, only the mode is set and the parameters of the mode are not set. When the length is 15, set the mode, set the parameters and save the parameters to EEPROM.
| 1112 | Timing_On_Off_Control |  | U16 |  |  | 0 | 1 | RW | Timed charging and discharging-enable control; Bit0: charge enable Bit1: discharge enable | end user
| 1113 | Timing_Charge_Start |  | U16 | 1 1 | Hours minutes | 0 0 | 23 59 | RW | High bytes. Charge start hour Low byte. Charge start minutes | end user
| 1114 | Timing_Charge_End |  | U16 | 1 1 | Hours minutes | 0 0 | 23 59 | RW | High Bytes. End of Charge Hour Low Byte. End of Charge Minutes | end user
| 1115 | Timing_Discharge_Start |  | U16 | 1 1 | Hours minutes | 0 0 | 23 59 | RW | High bytes. Discharge start hour Low byte. Discharge start minute | end user
| 1116 | Timing_Discharge_End |  | U16 | 1 1 | Hours minutes | 0 0 | 23 59 | RW | High bytes. Discharge End Hour Low Byte. End of Discharge Minutes | end user
| 1117 | Timing_Power_Charge |  | U32 | 1 | W | 1 | 4294967296 | RW | Timed charging and discharging - charging power | end user
| 1118 | [9 empty] | end user
| 1119 | Timing_Power_Discharge |  | U32 | 1 | W | 1 | 4294967296 | RW | Timed charging/discharging-discharging power | end user
| 111A | [9 empty] | end user
| 111B - 111E | Timing_Rsvd1 -- 4 | [7 empty] | Timed charging and discharging -- set aside 1-4 (4) | end user
| 111F | Timing_Control |  | U16 |  |  | 1 | 1 | RW | Timed Charge Write Control; On a write of 1, the value in the Timed Charge Shadow Register is updated to the system Timed Charge configuration; On read, the status of the last write operation is returned: 0x0000: Success 0x0001: operation in progress 0xFFFB: operation failed, the controller refuses to respond (maybe the controller is busy or misconfigured) 0xFFFC: operation failed, controller no answer 0xFFFD: operation failed, current function is disabled 0xFFFE: operation failed, parameter storage failed 0xFFFF: operation failed, input parameter is wrong | end user
time-sharing tariff | 1120 | TOU_ID |  | U16 |  |  | 0 | 7 | RW | Timesharing tariff-rule serial number; The smaller the serial number, the higher the priority. Upon successful write to this register, the time-of-day tariff parameter will be updated to the parameter corresponding to the serial number written. | end user | [6 empty] | When writing, the fixed first address is 0x1120 and the length is 1 or 16 When the length is 1, only the mode is set and the parameters of the mode are not set. When the length is 16, the mode is set, the parameters are set, and the parameters are saved to the EEPROM.
| 1121 | TOU_On_Off_Control |  | U16 |  |  | 0 | 1 | RW | Time-sharing tariff-rule enable; 0: disable 1: enable | end user
| 1122 | TOU_Charge_Start |  | U16 | 1 1 | Hours minutes | 0 0 | 23 59 | RW | High bytes. Charge start hour Low byte. Charge start minutes | end user
| 1123 | TOU_Charge_End |  | U16 | 1 1 | Hours minutes | 0 0 | 23 59 | RW | High Bytes. End of Charge Hour Low Byte. End of Charge Minutes | end user
| 1124 | TOU_Charge_Target_SOC |  | U16 | 1 | % | 30 | 100 | RW | Timeshare Tariff-Forced Charge Cutoff SOC; The percentage of remaining power, when the current SOC of the battery reaches this register value, the forced charging ends and enters the self-generation and self-consumption mode, while discharging is prohibited. | end user
| 1125 | TOU_Charge_Power |  | U32 | 1 | W | 1 | 4294967296 | RW | Timeshare Tariff - Forced Charging Power; The set value must not exceed the rated power of the machine. | end user
| 1126 | [9 empty] | end user
| 1127 | TOU_Executed_Date_Start |  | U16 | 1 1 | month day | 1 1 | 12 31 | RW | High Bytes. The month the rule goes into effect Low Byte. The date the rule went into effect | end user
| 1128 | TOU_Executed_Date_End |  | U16 | 1 1 | month day | 1 1 | 12 31 | RW | High Bytes. Month in which the rule ceased to be in effect Low Byte. The date the rule ceased to be in effect | end user
| 1129 | TOU_Executed_Day_of_Week |  | U16 |  |  |  |  | RW | Timeshare Tariff-Rule Effective Week; This register is represented as a bit field, with a bit 0 indicating an invalid week and a bit 1 indicating an effective week Bit0: Monday Bit1: Tuesday Bit2: Wednesday Bit3: Thursday Bit4: Friday Bit5: Saturday Bit6: Sunday | end user
| 112A - 112E | TOU_Rsvd1 -- 5 | [7 empty] | Time-of-use tariffs - set-aside 1-5 | end user
| 112F | TOU_Control |  | U16 |  |  | 1 | 1 | RW | Time-of-day tariff-write control; On a write value of 1, the value in the time-of-day tariff shadow register is updated to the system time-of-day tariff configuration; On read, the status of the last write operation is returned: 0x0000: Success 0x0001: operation in progress 0xFFFB: operation failed, the controller refuses to respond (maybe the controller is busy or misconfigured) 0xFFFC: operation failed, controller no answer 0xFFFD: operation failed, current function is disabled 0xFFFE: operation failed, parameter storage failed 0xFFFF: operation failed, input parameter is wrong | end user
peak reduction mode | 1130 -- 1131 | Peak_Shaving_Discharge_Threshold |  | U32 | 1 | W | 100 |  | RW | Upper limit on the amount of power the system is allowed to buy from the grid | end user | [6 empty] | This parameter is the parameter setting for clipping mode. When writing, the fixed first address is 0x1130 and the length is 4
| 1132 -- 1133 | Peak_Shaving_Charge_Threshold |  | U32 | 1 | W | 100 |  | RW | Upper limit on the amount of power the system is allowed to sell to the grid | end user
| 1134 -- 113F | [8 empty] | reserve
| 1140 -- 1143 | AddressMask_Config_Remote2 |  | U64 |  |  |  |  | R | Mask area for the 64 register address words starting at this address. Refer to the description of address 0x0040 | end user | 0 | 0000000F |  |  |  |  | Used to distinguish which addresses are valid and which are invalid, the main function is that different models use different registers, through the mask to do the distinction. This area supports arbitrary reading.
offline mode | 1144 | Off_Grid_Charge_Source |  | U16 |  |  | 0 | 2 | RW | Off Grid Mode - Charging source selection: 0: Grid 1: Generator 2: Reserved | [7 empty] | When writing, the fixed first address is 0x1144 and the length is 3. There is a special case where data of length 1 can be written from the first address 0x1146 alone.
| 1145 | Off_Grid_Grid_Power |  | U16 | 0.01 | kW | 0 | 65535 | RW | Off-grid mode - grid pickup power
| 1146 | Off_Grid_DG_Power |  | U16 | 0.01 | kW | 0 | 65535 | RW | Off-grid mode - Maximum generator withdrawal power
| 1147 - 117F | [8 empty] | reserve
| 1180 -- 1183 | AddressMask_Config_Remote3 |  | U64 |  |  |  |  | R | Mask area for the 64 register address words starting at this address. Refer to the description of address 0x0040 | end user | 0 | 0000000F |  |  |  |  | Used to distinguish which addresses are valid and which are invalid, the main function is that different models use different registers, through the mask to do the distinction. This area supports arbitrary reading.
passive mode | 1184 | Passive_Timeout |  | U16 | 1 | unit of angle or arc equivalent one sixtieth of a degree | 0 | 65535 | RW | Passive mode - timeout control; Default value: 0; Sets the passive mode communication timeout time, when the inverter does not receive any communication for more than the time set in this register, the inverter forces a timeout action. Exceptionally, writing 0 to this register will disable the timeout function. | end user | [6 empty] | When writing, the fixed first address is 0x1184 and the length is 2
| 1185 | Passive_Timeout_Action |  | U16 |  |  | 0 | 1 | RW | Passive Mode-Timeout Action; 0: forced standby 1: forced return to energy storage mode before entering passive mode | end user
| 1186 | Passive_Rsvd1 | [7 empty] | Passive mode - set aside 1 | end user
Manual Mode | 1187 | Passive_Manual_Gdes |  | I32 | 1 | W | -2147483648 | 2147483647 | RW | Manual mode expects grid power (Gdes); Positive values indicate the power direction "from grid to system"; Negative values indicate power direction "from system to grid"; Variable registers. | end user | [6 empty] | When writing, the fixed first address is 0x1187 and the length is 6. In this case there is a special case where data of length 4 can be written from the first address 0x1189 alone.
| 1188 | [7 empty] | RW |  | end user
| 1189 | Passive_Manual_Blo |  | I32 | 1 | W | -2147483648 | 2147483647 | RW | Minimum charging and discharging power (Blo) for Manual mode batteries; Positive values indicate charging; Negative values indicate discharging; Variable register. | end user
| 118A | [7 empty] | RW |  | end user
| 118B | Passive_Manual_Bup |  | I32 | 1 | W | -2147483648 | 2147483647 | RW | Maximum charging and discharging power (Bup) for Manual mode batteries; Positive values indicate charging; Negative values indicate discharging; Variable register. | end user
| 118C | [7 empty] | RW |  | end user
| 118D | Passive_Manual_Gdzup |  | I32 | 1 | W | -2147483648 | 2147483647 | RW | Manual mode allows to sell power (Gdzup); Positive values indicate the power direction "from grid to system"; Negative values indicate the power direction "from system to grid"; Variable registers. | end user | [6 empty] | Parameters are not used at the moment, they can be read but not written.
| 118E | [7 empty] | RW |  | end user
| 118F | Passive_Manual_Gdzlo |  | I32 | 1 | W | -2147483648 | 2147483647 | RW | Manual mode allows to buy electrical power (Gdzlo); Positive values indicate the power direction "from grid to system"; Negative values indicate the power direction "from system to grid"; Variable registers. | end user
| 1190 | [7 empty] | RW |  | end user
Scheduler Model | 1191 | Passive_Scheduler_Gdes_Ante |  | I32 | 1 | W | -2147483648 | 2147483647 | RW | Scheduler mode desired grid power (Gdes_Ante); Scheduled task parameter, valid for the scheduled time period. A positive value indicates the power direction "from grid to system"; Negative values indicate the power direction "from system to grid". | end user
| 1192 | [9 empty] | end user
| 1193 | Passive_Scheduler_Blo_Ante |  | I32 | 1 | W | -2147483648 | 2147483647 | RW | Minimum charging and discharging power of the Scheduler mode battery (Blo_Ante); Scheduled task parameter, valid for the scheduled time period. A positive value indicates the power direction "from grid to system"; Negative values indicate the power direction "from system to grid". | end user
| 1194 | [9 empty] | end user
| 1195 | Passive_Scheduler_Bup_Ante |  | I32 | 1 | W | -2147483648 | 2147483647 | RW | Scheduler mode battery maximum charge/discharge power (Bup_Ante); Scheduled task parameter, valid for the scheduled time period. A positive value indicates the power direction "from grid to system"; Negative values indicate the power direction "from system to grid". | end user
| 1196 | [9 empty] | end user
| 1197 | Passive_Scheduler_Gdzup_Ante |  | I32 | 1 | W | -2147483648 | 2147483647 | RW | Scheduler mode allows selling electrical power (Gdzup_Ante); Scheduled task parameter, valid for the scheduled time period. Positive values indicate the power direction "from grid to system"; Negative values indicate the power direction "from system to grid". | end user
| 1198 | [9 empty] | end user
| 1199 | Passive_Scheduler_Gdzlo_Ante |  | I32 | 1 | W | -2147483648 | 2147483647 | RW | Scheduler mode allows to buy electric power (Gdzlo_Ante); Scheduled task parameter, valid for the scheduled time period. Positive values indicate the power direction "from grid to system"; Negative values indicate the power direction "from system to grid". | end user
| 119A | [9 empty] | end user
| 119B | Passive_Scheduler_Gdes_Post |  | I32 | 1 | W | -2147483648 | 2147483647 | RW | Scheduler mode desired grid power (Gdes_Post); Scheduled task parameter, valid after the scheduled time period. A positive value indicates the power direction "from grid to system"; Negative values indicate the power direction "from system to grid". | end user
| 119C | [9 empty] | end user
| 119D | Passive_Scheduler_Blo_Post |  | I32 | 1 | W | -2147483648 | 2147483647 | RW | Minimum charging and discharging power of the Scheduler mode battery (Blo_Post); Scheduled task parameter, valid after the scheduled time period. A positive value indicates the power direction "from grid to system"; Negative values indicate the power direction "from system to grid". | end user
| 119E | [9 empty] | end user
| 119F | Passive_Scheduler_Bup_Post |  | I32 | 1 | W | -2147483648 | 2147483647 | RW | Scheduler mode battery maximum charge/discharge power (Bup_Post); Scheduled task parameter, valid after the scheduled time period. A positive value indicates the power direction "from grid to system"; Negative values indicate the power direction "from system to grid". | end user
| 11A0 | [9 empty] | end user
| 11A1 | Passive_Scheduler_Gdzup_Post |  | I32 | 1 | W | -2147483648 | 2147483647 | RW | Scheduler mode allows selling power (Gdzup_Post); Scheduled task parameter, valid after the scheduled time period. A positive value indicates the power direction "from grid to system"; Negative values indicate the power direction "from system to grid". | end user
| 11A2 | [9 empty] | end user
| 11A3 | Passive_Scheduler_Gdzlo_Post |  | I32 | 1 | W | -2147483648 | 2147483647 | RW | Scheduler mode allows to buy electrical power (Gdzlo_Post); Scheduled task parameter, valid after the scheduled time period. Positive values indicate the power direction "from grid to system"; Negative values indicate the power direction "from system to grid". | end user
| 11A4 | [9 empty] | end user
| 11A5 | Passive_Scheduler_StartTime |  | U32 | 1 | unit of angle or arc equivalent one sixtieth of a degree | 0 | 4294967296 | RW | Scheduler mode applies the start time of the desired parameter setting; StartTime is a unix time format, because the system internal time defaults to Greenwich Mean Time (GMT), so when setting this parameter, you should pay attention to the local time zone of the country, StartTime = (local Unix Time) ± (the number of seconds corresponding to the time difference between local time and UTC/GMT) | end user
| 11A6 | [9 empty] | end user
| 11A7 | Passive_Scheduler_DurationTime |  | U32 | 1 | unit of angle or arc equivalent one sixtieth of a degree | 0 | 4294967296 | RW | DurationTime for Scheduler mode to apply desired parameter setpoints | end user
| 11A8 | [9 empty] | end user
| 11A9 | Passive_Scheduler_ManagementMode |  | U16 |  |  | 0 | 2 | RW | Scheduler mode ManagementMode selection; 0: Spontaneous mode 1: Manual mode 2: Scheduler mode Only 0, 1 and 2 can be entered, other data is invalid. | end user
| 11AA -- 11BF | [8 empty] | reserve
| 11C0 -- 11C3 | AddressMask_Config_Remote4 |  | U64 |  |  |  |  | R | Mask area for the 64 register address words starting at this address. Refer to the description of address 0x0040 | end user | 0 | 0000000F |  |  |  |  | Used to distinguish which addresses are valid and which are invalid, the main function is that different models use different registers, through the mask to do the distinction. This area supports arbitrary reading.
Power station communication interruption protection function | 11C4 | CommBreak_Protect_Enable |  | U16 | 1 |  | 0 | 65535 | RW | Power station communication interrupt protection function enable register: 0: Power station communication interrupt protection function disable (default) 1: Power plant communication interrupt protection function enable | [7 empty] | Parameters not used at this time
| 11C5 | CommBreak_Recovery_Mode |  | U16 | 1 |  | 0 | 65535 | RW | Power station communication interruption protection recovery method: 0: automatic recovery (default) 1: Manual recovery
| 11C6 | CommBreak_Threshold_Time |  | U16 | 1 | min | 10 | 120 | RW | Power station communication interruption threshold time: 10-120min (default:15min)
| 11C7 | CommBreak_Mode_Judge |  | U16 | 1 |  | 0 | 65535 | RW | Data monitoring source for power station communication outages: 0: 485 (default) 1: WIFI 3: PLC
| 11C8 | CommBreak_Alarm_Clear |  | U16 | 1 |  | 0 | 65535 | W | The station communication interruption alarm clear register: Write "1" to clear the communication interrupt alarm status.
| 1200-1203 | reserved |  | U16 |  |  |  |  | R | reservations
EMS Parameter Configuration 1 | 1204 | period_control |  | U16 |  |  |  |  | RW | Enable control bits for each time slot bit0-5: corresponds to time slots 1-6 | [7 empty] | BMSconfiguration parameters need to beset togethertime periods1-6, individual settings are invalid
| 1205 | period1_time_start |  | U16 |  |  |  |  | RW | Slot 1 start time High Byte Hour Low Byte Minutes
| 1206 | period1_time_end |  | U16 |  |  |  |  | RW | Slot 1 End Time High Byte Hour Low Byte Minutes
| 1207 | period1_ems_mode |  | U16 |  |  |  |  | RW | Slot 1emsmode 0: photovoltaic 1: constant power mode 2: Self-generation and self-consumption 3: peak shaving and valley filling 4: Demand control 5: Battery forced charging mode 6: Battery forced discharge mode
| 1208 | period1_PCC_limit_up |  | I16 |  | 0.01kw |  |  | RW | Time slot 1 grid point power limit
| 1209 | period1_PCC_limit_down |  | I16 |  | 0.01kw |  |  | RW | Lower power limit for time slot one and grid point
| 120A | period1_SOC_H |  | U16 | 1 | % | 0 | 100 | RW | Maximum permissible charging limit for time period 1 battery
| 120B | period1_SOC_L |  | U16 | 1 | % | 0 | 100 | RW | Lower limit of permissible battery discharge for time period 1
| 120C | period1_Enable_charge_from_grid |  | U16 |  |  | 0 | 1 | RW | Whether or not the grid is allowed to charge the system during time period one | [7 empty] | Useful only in constant power mode
| 120D | period1_Pinv_set |  | I16 |  | 0.01kw |  |  | RW | Time period 1 inverter power | [7 empty] | Useful only in battery-forced mode
| 120E | period1_Pdc_set |  | I16 |  | 0.01kw |  |  | RW | Time period 1 forced charge/discharge power (total battery port power) | [7 empty] | Useful only in spontaneous use mode
| 120F | period1_Enable_Id_add |  | U16 |  |  | 0 | 1 | RW | Whether self-generated excess power is allowed to be fed into the network during time period 1
| 1210 | period1_rsvd1 |  | U16 |  |  |  |  | RW | Reservation for time slot 1
| 1211 | period1_rsvd2 |  | U16 |  |  |  |  | RW | Reservation for time slot 1
| 1212 | period2_time_start |  | U16 |  |  |  |  | RW | Slot 1 start time High Byte Hour Low Byte Minutes
| 1213 | period2_time_end |  | U16 |  |  |  |  | RW | Slot 1 End Time High Byte Hour Low Byte Minutes
| 1214 | period2_ems_mode |  | U16 |  |  |  |  | RW | Slot 2emsmode 0: photovoltaic 1: constant power mode 2: Self-generation and self-consumption 3: peak shaving and valley filling 4: Demand control 5: Battery forced charging mode 6: Battery forced discharge mode
| 1215 | period2_PCC_limit_up |  | I16 |  | 0.01kw |  |  | RW | Power limit for grid-connected points in time period 2
| 1216 | period2_PCC_limit_down |  | I16 |  | 0.01kw |  |  | RW | Lower limit of power at grid-connected points for time period 2
| 1217 | period2_SOC_H |  | U16 | 1 | % | 0 | 100 | RW | Maximum permissible charging limit for time period 2 batteries
| 1218 | period2_SOC_L |  | U16 | 1 | % | 0 | 100 | RW | Lower limit of permissible battery discharge for time period 2
| 1219 | period2_Enable_charge_from_grid |  | U16 |  |  | 0 | 1 | RW | Whether or not the grid is allowed to charge the system during time period 2
| 121A | period2_Pinv_set |  | I16 |  | 0.01kw |  |  | RW | Slot 2 Inverter Power
| 121B | period2_Pdc_set |  | I16 |  | 0.01kw |  |  | RW | Forced charging and discharging power (total battery port power) for time period 2
| 121C | period2_Enable_Id_add |  | U16 |  |  | 0 | 1 | RW | Whether self-generated excess power is allowed to be fed into the network in time slot 2
| 121D | period2_rsvd1 |  | U16 |  |  |  |  | RW | Reservation for time slot 2
| 121E | period2_rsvd2 |  | U16 |  |  |  |  | RW | Reservation for time slot 2
| 121F | period3_time_start |  | U16 |  |  |  |  | RW | Slot 1 start time High Byte Hour Low Byte Minutes
| 1220 | period3_time_end |  | U16 |  |  |  |  | RW | Slot 1 End Time High Byte Hour Low Byte Minutes
| 1221 | period3_ems_mode |  | U16 |  |  |  |  | RW | Time period threeemsmode 0: photovoltaic 1: constant power mode 2: Self-generation and self-consumption 3: peak shaving and valley filling 4: Demand control 5: Battery forced charging mode 6: Battery forced discharge mode
| 1222 | period3_PCC_limit_up |  | I16 |  | 0.01kw |  |  | RW | Time period three parallel network point power limit
| 1223 | period3_PCC_limit_down |  | I16 |  | 0.01kw |  |  | RW | Lower limit of power at time period three parallel points
| 1224 | period3_SOC_H |  | U16 | 1 | % | 0 | 100 | RW | Maximum permissible battery charge for time period 3
| 1225 | period3_SOC_L |  | U16 | 1 | % | 0 | 100 | RW | Lower limit of permissible battery discharge for time period 3
| 1226 | period3_Enable_charge_from_grid |  | U16 |  |  | 0 | 1 | RW | Whether or not the grid is allowed to charge the system during time period three
| 1227 | period3_Pinv_set |  | I16 |  | 0.01kw |  |  | RW | Slot 3 Inverter Power
| 1228 | period3_Pdc_set |  | I16 |  | 0.01kw |  |  | RW | Time period 3 forced charge/discharge power (total battery port power)
| 1229 | period3_Enable_Id_add |  | U16 |  |  | 0 | 1 | RW | Whether self-generated excess power is allowed to be fed into the network in time slot 3
| 122A | period3_rsvd1 |  | U16 |  |  |  |  | RW | Reservation for time slot 3
| 122B | period3_rsvd2 |  | U16 |  |  |  |  | RW | Reservation for time slot 3
| 122C | period4_time_start |  | U16 |  |  |  |  | RW | Slot 1 start time High Byte Hour Low Byte Minutes
| 122D | period4_time_end |  | U16 |  |  |  |  | RW | Slot 1 End Time High Byte Hour Low Byte Minutes
| 122E | period4_ems_mode |  | U16 |  |  |  |  | RW | Slot fouremsmode 0: photovoltaic 1: constant power mode 2: Self-generation and self-consumption 3: peak shaving and valley filling 4: Demand control 5: Battery forced charging mode 6: Battery forced discharge mode
| 122F | period4_PCC_limit_up |  | I16 |  | 0.01kw |  |  | RW | Power ceiling for grid-connected points in time slot 4
| 1230 | period4_PCC_limit_down |  | I16 |  | 0.01kw |  |  | RW | Lower limit of power at grid-connected points for time period 4
| 1231 | period4_SOC_H |  | U16 | 1 | % | 0 | 100 | RW | Maximum permissible charging limit for time period 4 batteries
| 1232 | period4_SOC_L |  | U16 | 1 | % | 0 | 100 | RW | Lower limit of permissible battery discharge for time period 4
| 1233 | period4_Enable_charge_from_grid |  | U16 |  |  | 0 | 1 | RW | Whether or not the grid is allowed to charge the system during time period four
| 1234 | period4_Pinv_set |  | I16 |  | 0.01kw |  |  | RW | Slot 4 Inverter Power
| 1235 | period4_Pdc_set |  | I16 |  | 0.01kw |  |  | RW | Time period 4 mandatory charging and discharging power (total battery port power)
| 1236 | period4_Enable_Id_add |  | U16 |  |  | 0 | 1 | RW | Whether self-generated excess power is allowed to be fed into the grid in time slot 4
| 1237 | period4_rsvd1 |  | U16 |  |  |  |  | RW | Reservation for time slot 4
| 1238 | period4_rsvd2 |  | U16 |  |  |  |  | RW | Reservation for time slot 4
1239
123A
123B
123C
123D
123E
123F
| 1240-1243 | reserved |  | U16 |  |  |  |  | R | reservations
EMS Parameter Configuration 2 | 1244 | period5_time_start |  | U16 |  |  |  |  | RW | Slot 1 start time High Byte Hour Low Byte Minutes | [7 empty] | This segment register needs to be connected to the
| 1245 | period5_time_end |  | U16 |  |  |  |  | RW | Slot 1 End Time High Byte Hour Low Byte Minutes
| 1246 | period5_ems_mode |  | U16 |  |  |  |  | RW | Time period fiveemsmode 0: photovoltaic 1: constant power mode 2: Self-generation and self-consumption 3: peak shaving and valley filling 4: Demand control 5: Battery forced charging mode 6: Battery forced discharge mode
| 1247 | period5_PCC_limit_up |  | I16 |  | 0.01kw |  |  | RW | Power limit for grid-connected points for time period 5
| 1248 | period5_PCC_limit_down |  | I16 |  | 0.01kw |  |  | RW | Lower limit of power at grid-connected points for time period 5
| 1249 | period5_SOC_H |  | U16 | 1 | % | 0 | 100 | RW | Maximum permissible battery charge for time period 5
| 124A | period5_SOC_L |  | U16 | 1 | % | 0 | 100 | RW | Lower limit of permissible battery discharge for time period 5
| 124B | period5_Enable_charge_from_grid |  | U16 |  |  | 0 | 1 | RW | Whether time slot 5 allows the grid to charge the system
| 124C | period5_Pinv_set |  | I16 |  | 0.01kw |  |  | RW | Slot V Inverter Power
| 124D | period5_Pdc_set |  | I16 |  | 0.01kw |  |  | RW | Time period 5 forced charge/discharge power (total battery port power)
| 124E | period5_Enable_Id_add |  | U16 |  |  | 0 | 1 | RW | Whether self-generated excess power is allowed to be brought online in time slot 5
| 124F | period5_rsvd1 |  | U16 |  |  |  |  | RW | Reservation for time slot V
| 1250 | period5_rsvd2 |  | U16 |  |  |  |  | RW | Reservation for time slot V
| 1251 | period6_time_start |  | U16 |  |  |  |  | RW | Slot 6 Start Time High Byte Hour Low Byte Minutes
| 1252 | period6_time_end |  | U16 |  |  |  |  | RW | Slot 6 End Time High Byte Hour Low Byte Minutes
| 1253 | period6_ems_mode |  | U16 |  |  |  |  | RW | Slot sixemsmode 0: photovoltaic 1: constant power mode 2: Self-generation and self-consumption 3: peak shaving and valley filling 4: Demand control 5: Battery forced charging mode 6: Battery forced discharge mode
| 1254 | period6_PCC_limit_up |  | I16 |  | 0.01kw |  |  | RW | Power ceiling for grid connection points for time period 6
| 1255 | period6_PCC_limit_down |  | I16 |  | 0.01kw |  |  | RW | Lower power limit for grid connection points for time period 6
| 1256 | period6_SOC_H |  | U16 | 1 | % | 0 | 100 | RW | Maximum permissible charging limit for time slot 6 batteries
| 1257 | period6_SOC_L |  | U16 | 1 | % | 0 | 100 | RW | Lower limit of permissible battery discharge for time period 6
| 1258 | period6_Enable_charge_from_grid |  | U16 |  |  | 0 | 1 | RW | Whether or not time slot 6 allows the grid to charge the system
| 1259 | period6_Pinv_set |  | I16 |  | 0.01kw |  |  | RW | Slot 6 Inverter Power
| 125A | period6_Pdc_set |  | I16 |  | 0.01kw |  |  | RW | Time period six mandatory charging and discharging power (total battery port power)
| 125B | period6_Enable_Id_add |  | U16 |  |  | 0 | 1 | RW | Whether self-generated excess power is allowed to be fed into the network in time slot 6
| 125C | period6_rsvd1 |  | U16 |  |  |  |  | RW | Reservation for Slot 6
| 125D | period6_rsvd2 |  | U16 |  |  |  |  | RW | Reservation for Slot 6
4.3 Inverter return read-only result (0x1300-0x15FF) |  |  | Italy Auto Test, IV Scan, Historical Event Information
| 1300 -- 1303 | AddressMask_Config_ReadOnly_Result1 |  | U64 |  |  |  |  | R | Mask area for the 64 register address words starting at this address. Refer to the description of address 0x0040 |  | 0 | 0000000F |  |  |  |  | It is used to distinguish which addresses are valid and which are invalid, the main function is that different models use different registers, through the mask to do the distinction. This area only supports reading the mask, if you read the data in other areas, it will lead to abnormal function parameters and crash.
Automated testing in Italy | 1304 | Italy_Autotest_Result1 |  | U16 | 0.1 | V |  |  | R | Italy automatic test 59.s1. Default setting of the first level of overvoltage protection value.
| 1305 | Italy_Autotest_Result2 |  | U16 | 1 | ms |  |  | R | Italy automatic test 59.s1. Default setting for one level of overvoltage protection time.
| 1306 | Italy_Autotest_Result3 |  | U16 | 0.1 | V |  |  | R | Italian automatic test 59.s1. Test results of the first level of overvoltage protection value.
| 1307 | Italy_Autotest_Result4 |  | U16 | 1 | ms |  |  | R | Italian automatic test 59.s1. Results of the first level overvoltage protection time test.
| 1308 | Italy_Autotest_Result5 |  | U16 | 0.1 | V |  |  | R | Italy auto test 59.s2. Default setting of the secondary overvoltage protection value.
| 1309 | Italy_Autotest_Result6 |  | U16 | 1 | ms |  |  | R | Italy auto test 59.s2. Default setting for secondary overvoltage protection time.
| 130A | Italy_Autotest_Result7 |  | U16 | 0.1 | V |  |  | R | Italian automatic test 59.s2. Test results of secondary overvoltage protection value.
| 130B | Italy_Autotest_Result8 |  | U16 | 1 | ms |  |  | R | Italian automatic test 59.s2. Secondary overvoltage protection time test results.
| 130C | Italy_Autotest_Result9 |  | U16 | 0.1 | V |  |  | R | Italy automatic test 27.s1. Default setting of the first level of undervoltage protection value.
| 130D | Italy_Autotest_Result10 |  | U16 | 1 | ms |  |  | R | Italy automatic test 27.s1. Default setting for one level of undervoltage protection time.
| 130E | Italy_Autotest_Result11 |  | U16 | 0.1 | V |  |  | R | Italian automatic test 27.s1. Test results of the first level of undervoltage protection value.
| 130F | Italy_Autotest_Result12 |  | U16 | 1 | ms |  |  | R | Italian automatic test 27.s1. First level undervoltage protection time test results.
| 1310 | Italy_Autotest_Result13 |  | U16 | 0.1 | V |  |  | R | Italy automatic test 27.s2. Default setting of the secondary undervoltage protection value.
| 1311 | Italy_Autotest_Result14 |  | U16 | 1 | ms |  |  | R | Italy auto test 27.s2. Default setting for secondary undervoltage protection time.
| 1312 | Italy_Autotest_Result15 |  | U16 | 0.1 | V |  |  | R | Italian automatic test 27.s2. Test results of secondary undervoltage protection value.
| 1313 | Italy_Autotest_Result16 |  | U16 | 1 | ms |  |  | R | Italian automatic test 27.s2. Secondary undervoltage protection time test results.
| 1314 | Italy_Autotest_Result17 |  | U16 | 0.01 | Hz |  |  | R | Italy auto test 81&gt;s1. Default setting of the first level of overfrequency protection value.
| 1315 | Italy_Autotest_Result18 |  | U16 | 1 | ms |  |  | R | Italy auto test 81&gt;s1. Default setting for one level of overfrequency protection time.
| 1316 | Italy_Autotest_Result19 |  | U16 | 0.01 | Hz |  |  | R | Italian automatic test 81&gt;s1. Test results of the first level of overfrequency protection value.
| 1317 | Italy_Autotest_Result20 |  | U16 | 1 | ms |  |  | R | Italian automatic test 81&gt;s1. Results of the first level overfrequency protection time test.
| 1318 | Italy_Autotest_Result21 |  | U16 | 0.01 | Hz |  |  | R | Italy auto test 81&gt;s2. Default setting of the secondary overfrequency protection value.
| 1319 | Italy_Autotest_Result22 |  | U16 | 1 | ms |  |  | R | Italy auto test 81&gt;s2. Default setting for secondary overfrequency protection time.
| 131A | Italy_Autotest_Result23 |  | U16 | 0.01 | Hz |  |  | R | Italian automatic test 81&gt;s2. Test results of the secondary overfrequency protection value.
| 131B | Italy_Autotest_Result24 |  | U16 | 1 | ms |  |  | R | Italian automatic test 81&gt;s2. Results of the secondary overfrequency protection time test.
| 131C | Italy_Autotest_Result25 |  | U16 | 0.01 | Hz |  |  | R | Italy auto test 81&lt;s1. Default setting of the first level of underfrequency protection value.
| 131D | Italy_Autotest_Result26 |  | U16 | 1 | ms |  |  | R | Italy auto test 81&lt;s1. Default setting for one level of underfrequency protection time.
| 131E | Italy_Autotest_Result27 |  | U16 | 0.01 | Hz |  |  | R | Italian automatic test 81&lt;s1. Test results of the first level underfrequency protection value.
| 131F | Italy_Autotest_Result28 |  | U16 | 1 | ms |  |  | R | Italian automatic test 81&lt;s1. First level underfrequency protection time test results.
| 1320 | Italy_Autotest_Result29 |  | U16 | 0.01 | Hz |  |  | R | Italy auto test 81&lt;s2. Default setting of the secondary underfrequency protection value.
| 1321 | Italy_Autotest_Result30 |  | U16 | 1 | ms |  |  | R | Italy auto test 81&lt;s2. Default setting for secondary underfrequency protection time.
| 1322 | Italy_Autotest_Result31 |  | U16 | 0.01 | Hz |  |  | R | Italian automatic test 81&lt;s2. Test results for secondary underfrequency protection value.
| 1323 | Italy_Autotest_Result32 |  | U16 | 1 | ms |  |  | R | Italian automatic test 81&lt;s2. Secondary underfrequency protection time test results.
| 1324 -- 1333 | Italy_Autotest_Result33 -- 48 | [7 empty] | Italian automated test results 33-48 (16)
| 1334-133F | [8 empty] | reserve
| 1340 -- 1343 | AddressMask_Config_ReadOnly_Result2 |  | U64 |  |  |  |  | R | Mask area for the 64 register address words starting at this address. Refer to the description of address 0x0040 |  | 0 | 0000000F |  |  |  |  | This area only supports reading an area with a fixed first address.
IV curve scanning | 1344 - 137E | IVCurve_Voltage1 -- 30 |  | U16 | 0.1 | V |  |  | R | IV curve scanning voltage 1-30. | [7 empty] | 2 addresses apart
| 1345 - 137F | IVCurve_Current1 -- 30 |  | U16 | 0.01 | A |  |  | R | IV curve scanning current 1-30. | [7 empty] | 2 addresses apart
| 1380 -- 1383 | AddressMask_Config_ReadOnly_Result3 |  | U64 |  |  |  |  | R | Mask area for the 64 register address words starting at this address. Refer to the description of address 0x0040 |  | 0 | 0000000F |  |  |  |  | This area only supports reading an area with a fixed first address.
IV curve scanning | 1384 - 13BE | IVCurve_Voltage31 -- 60 |  | U16 | 0.1 | V |  |  | R | IV curve scanning voltage 31-60. | [7 empty] | 2 addresses apart
| 1385 - 13BF | IVCurve_Current31 -- 60 |  | U16 | 0.01 | A |  |  | R | IV curve scanning current 31-60. | [7 empty] | 2 addresses apart
| 13C0 - 13C3 | AddressMask_Config_ReadOnly_Result4 |  | U64 |  |  |  |  | R | Mask area for the 64 register address words starting at this address. Refer to the description of address 0x0040 |  | 0 | 0000000F |  |  |  |  | This area only supports reading an area with a fixed first address.
IV curve scanning | 13C4 - 13FE | IVCurve_Voltage61 -- 90 |  | U16 | 0.1 | V |  |  | R | IV curve scanning voltage 61-90. | [7 empty] | 2 addresses apart
| 13C5 - 13FF | IVCurve_Current61 -- 90 |  | U16 | 0.01 | A |  |  | R | IV curve scanning current 61-90. | [7 empty] | 2 addresses apart
| 1400 --1403 | AddressMask_Config_ReadOnly_Result5 |  | U64 |  |  |  |  | R | Mask area for the 64 register address words starting at this address. Refer to the description of address 0x0040 |  | 0 | 0000000F |  |  |  |  | This area only supports reading an area with a fixed first address.
IV curve scanning | 1404 -- 143E | IVCurve_Voltage91 -- 120 |  | U16 | 0.1 | V |  |  | R | IV curve scanning voltage 91-120. | [7 empty] | 2 addresses apart
| 1405 -- 143F | IVCurve_Current91 -- 120 |  | U16 | 0.01 | A |  |  | R | IV curve scanning current 91-120. | [7 empty] | 2 addresses apart
| 1440 -- 1443 | AddressMask_Config_ReadOnly_Result6 |  | U64 |  |  |  |  | R | Mask area for the 64 register address words starting at this address. Refer to the description of address 0x0040 |  | 0 | 0000000F |  |  |  |  | This area only supports reading an area with a fixed first address.
IV curve scanning | 1444 - 147E | IVCurve_Voltage121 -- 150 |  | U16 | 0.1 | V |  |  | R | IV curve scanning voltage 121-150. | [7 empty] | 2 addresses apart
| 1445 - 147F | IVCurve_Current121 -- 150 |  | U16 | 0.01 | A |  |  | R | IV curve scanning current 121-150. | [7 empty] | 2 addresses apart
historical incident | 1480 -- 160C | HistoryEventList_ID1 -- 100 |  | U16 |  |  |  |  | R | Historical event ID most recent 1-100th (of 100). | [7 empty] | Each ID is spaced 4 addresses apart When read, these form the ID of the 1st historical fault message and the trigger time. A single read within the range will always read the event ID, only four registers together will read the complete data. Up to 10 historical data can be read at once
| 1481 -- 160D | HistoryEventList_yM1 -- 100 |  | U16 |  |  |  |  | R | Historical event time most recent 1-100th entry (out of 100). High byte: the two lower digits of the year decimal number; Low byte: month.
| 1482 -- 160E | HistoryEventList_dH1 -- 100 |  | U16 |  |  |  |  | R | Historical event time most recent 1-100th entry (of 100). High byte: date; Low byte: hour.
| 1483 -- 160F | HistoryEventList_ms1 -- 100 |  | U16 |  |  |  |  | R | Historical event time most recent 1-100th entry (of 100). High byte: minutes; Low byte: seconds.
Historical Electricity | 1610 -- 165E | EnergyStatistics1 - 40 |  | U32 | 0.01 | kWh |  |  | R | Historical Power Statistics Entries 1-40 (40). the U32 is spaced 2 addresses at a time. Corresponding date and time refer to the Power Statistics Return Setting Register. | [7 empty] | The reading of this area is related to the setting of address 0x1030 to 0x1033, which shows all the power data, and you need to set the value of 0x1030 to 0x1033 before reading. If it is year, then the first 12 data represent the power data of 12 months. If it is a month, then the first 31 data represent the power data of 31 days.
1611 -- 165F
4.4 Core Function Configuration (0x2000-0x207F) |  |  | Restore factory settings, safety file (country/standard/version) information setting, local and remote upgrade control, upgrade progress
| 2000 -- 2003 | AddressMask_Config_Core1 |  | U64 |  |  |  |  | R | Mask area for the 64 register address words starting at this address. Refer to the description of address 0x0040 |  | 0 | 0000000F |  |  |  |  | Used to distinguish which addresses are valid and which are invalid, the main function is that different models use different registers, through the mask to do the distinction. This area supports arbitrary reading.
safety net | 2004 | Country_Code |  | U16 |  |  |  |  | RW | Safety countries for storage | [7 empty] | When writing, the fixed first address is 0x2004 and the length is 2
Safety Versions | 2005 | Safety_Version |  | U16 |  |  |  |  | RW | The version number of the safety parameter of the communication host (upper computer).
User data reset | 2006 | UserDataReset |  | U16 |  |  | 1 | 255 | RW | Restores the factory register; Bit value of 1 is valid. Bit0: Clear power level Bit1: clear event log Bit2: Restore default values for all function configuration parameters When reading, return to the status of the last write operation: 0x0000: Success 0x0001-0x00FF: operation in progress 0xFFFB: operation failed, controller refuses to respond (maybe the controller is busy or misconfigured) 0xFFFC: operation failed, controller no answer 0xFFFD: operation failed, current function is disabled 0xFFFE: operation failed, parameter access failed 0xFFFF: operation failed, input parameter is wrong | [7 empty] | When writing, the fixed first address is 0x2006 and the length is 1
Name of the country of safety regulations | 2007 -- 200B | Safety_Name1 -- 5 |  | ASCII |  |  |  |  | RW | Bits 1-10 of the safety country name. Each address represents 2 bits, as an example below, and so on. Register 0x2007 high 8 bits holds the safety regulation name bit 1; Register 0x2007 low 8 bits holds the safety regulation name bit 2. | [7 empty] | The data in this area is not used for the time being and is meaningless.
| 200C | [8 empty] | reserve
Upper communication protocol setting | 200D | Commu_protocol_type |  | U16 |  |  |  |  | RW | Protocol setting register: 0x0000:modbus_RTU protocol; 0x0001:modbus_Korea protocol; 0x0002:sofar_sgp_normal standard version protocol; 0x0003:sofar_sgp_advance advanced version protocol; 0x0004:sunspec protocol; 0x0005:solarmax protocol;
Safety documentation package setup | 200E | Country_Code_flash |  | U16 |  |  |  |  | RW | Safety standards for setting up the safety file package in FLASH | [7 empty] | When writing, the fixed first address is 0x200E and the length is 2
| 200F | Safety_Version_flash |  | U16 |  |  |  |  | RW | The version number of the safety documentation package in FLASH.
| 2010 -- 2033 | [8 empty] | reserve
Local and Remote Firmware upgrade control | 2034 | Remote_Download_Control_ex |  | U16 |  |  |  |  | W | Remote download control register extension. (only single target operations are supported) High Byte. Write to 0xA5 is valid. The low byte contains the combination of chips to be upgraded, with each bit explained as follows: Bit0: DCDC-ARM; Bit1: DCDC-DSP; | [7 empty] | The data in this area is not used for the time being and is meaningless.
| 2035 | Remote_Upgrade_Control_ex |  | U16 |  |  |  |  | W | Remote upgrade control register extension. (only single target operations are supported) High Byte. Write to 0xA5 is valid. The low byte contains the combination of chips to be upgraded, and each bit is explained as follows: Bit0: DCDC-ARM; Bit1: DCDC-DSP;
| 2036 | Local_Upgrade_Control_ex |  | U16 |  |  |  |  | W | Local Upgrade Control Extension 1. High Byte. Write to 0xA5 is valid. The low byte contains the combination of chips to be upgraded, and each bit is explained as follows: Bit0: DCDC-ARM; Bit1: DCDC-DSP;
| 2037 | Local_Upgrade_Control2 |  | U16 |  |  |  |  | W | Local Upgrade Control Extension 2. High Byte. Single BIN file upgrade writes 0xA5 sofar packaged files written to 0x80 Low Byte. The low byte contains the combination of chips to be upgraded, refer to the "Chip Corner and File Type Encoding" document. color and file type encoding" document, if it is sofar file fixed Write 0xFF | [7 empty] | When writing, the fixed first address is 0x2037 and the length is 1
| 2038 | Local_Upgrade_Status2 |  | U16 |  |  |  |  | R | Current upgrade progress The high byte indicates the type of target file currently being upgraded. 0x00:APP. 0x01: CORE. 0x02: safety file. 0xff: sofar package Low byte indicates current upgrade progress: progress range 0-100%: 0x00: APP: 0x01: CORE; 0x02: safety file; 0xff: sofar package.
| 2039 | Upgrade_Total |  | U16 |  |  |  |  | R | Total number of upgrade targets. When one or more targets are upgraded simultaneously using the same firmware, the value of this register indicates the total number of upgrade targets.
| 203A | Upgrade_Result_Table1 |  | U16 |  |  |  |  | R | Upgrade results bit Table 1. A bit value of 0 indicates that the upgrade was not completed or failed; A bit value of 1 indicates that the upgrade was successful. The lowest bit indicates the upgrade target numbered 1. The highest bit indicates the upgrade target numbered 16.
| 203B | Upgrade_Result_Table2 |  | U16 |  |  |  |  | R | Upgrade results bit Table 2. A bit value of 0 indicates that the upgrade was not completed or failed; A bit value of 1 indicates that the upgrade was successful. The lowest bit indicates upgrade target number 17. The highest bit indicates upgrade target number 32.
| 203C | Remote_Download_Control |  | U16 |  |  |  |  | W | Remote download of control registers. (Only single target operation is supported) | [7 empty] | High Byte. Write to 0xA5 is valid. The low byte contains the combination of chips to be upgraded, and each bit is explained as follows: Bit0: communication board; Bit1: control board 1 (primary DSP); Bit2: Control board 2 (secondary DSP); Bit3: Fuse; Bit4: BMS; Bit5: PCU; Bit6: BDU; Bit7: AFCI;
| 203D | Remote_Upgrade_Control |  | U16 |  |  |  |  | W | Remote Upgrade Control Register. High Byte: Single BIN file upgrade writes to 0xA5 sofar packaged file written to 0x80 Low Byte: The low byte contains the combination of chips that need to be upgraded, refer to the Chip Role and File Type Encoding document, if it is a sofar file fixed write 0xFF
| 203E | Local_Upgrade_Control |  | U16 |  |  |  |  | W | Local Upgrade Control Register. (only supports single-target operations), written with a fixed first address of 0x203E and a length of 1
| 203F | Local_Upgrade_Status |  | U16 |  |  |  |  | R | Current upgrade progress The high byte indicates the target chip for the current upgrade: 0x00: not in upgrade state; 0x01: primary DSP upgrade; 0x02: secondary DSP upgrade; 0x03: ARM upgrade; 0x04: FUSE upgrade; 0x05: BMS upgrade; 0x06: PCU upgrade; 0x07: BDU upgrade; 0x28: DC/DC ARM upgrade; 0x29: DC/DC DSP upgrade; 0x42: AFCI upgrade Refer to SVN "Chip Role and File Type Encoding" for subsequent reference The low byte indicates the current upgrade progress: progress range 0-100%; | [7 empty] | When this register has a value, one of registers 0x203D or 0x203E must have a value
| 2040-2045 | Upgrade_Time |  | U16 |  |  |  |  | RW | Timed Upgrade Time Register 0x2040:Timed upgrade time - year Register 0x2041:Timed upgrade time - month Register 0x2042:Timed Upgrade Time-Day Register0x2043:Timed upgrade time - hour Register 0x2044:Timed upgrade time-minute Register 0x2045:Timed upgrade time-seconds The value of time register is all 0XFF means cancel timer upgrade.
| 2046 | Upgrade_Result |  | U16 |  |  |  |  | R | Upgrade Result Bit0-Bit7: Number of devices upgraded this time Bit8-Bit15: Whether the statistics of this upgrade result is completed or not 0xA5: result counting is completed Other values: results are being counted If the value of this field is 0xA5, it is valid to read the upgrade result from register 0x2047. This register will be reset after receiving the upgrade command.
| 2047 | Upgrade_Result1 |  | U16 |  |  |  |  | R | Upgrade Result Number of successful device upgrades This register is reset upon receipt of an upgrade command.
| 2048 | Upgrade_Result_target |  | U16 |  |  |  |  | W | Upgrade result query control register APP and monitoring platform write the code of the upgrade object to be queried into this register, which is based on the code defined in the document "Chip Role and File Type Code". Write to this register and then get the upgrade result from 0x2046 and 0x2047 registers.
Chip Character Upgrade Progress | 2049 | Local_Upgrade_Safety_Status |  | U16 |  |  |  |  | R | The current upgrade progress of the safety file, the high byte indicates the upgrade status: 0x00: not in upgrade status; 0x01: being upgraded; 0x02: upgrade failed; 0x03: upgrade successful; Other: invalid; The low byte indicates the current upgrade progress: progress range 0-100%;
| 204A | Local_Upgrade_Sofar_Status |  | U16 |  |  |  |  | R | Current upgrade progress of Sofar package, high byte indicates upgrade status: 0x00: not in upgrade status; 0x01: being upgraded; 0x02: upgrade failed; 0x03: upgrade successful; Other: invalid; The low byte indicates the current upgrade progress: progress range 0-100%;
| 204B | Local_Upgrade_Core_Status |  | U16 |  |  |  |  | R | Core current upgrade progress, high byte indicates upgrade status: 0x00: not in upgrade status; 0x01: being upgraded; 0x02: upgrade failed; 0x03: upgrade successful; Other: invalid; The low byte indicates the current upgrade progress: progress range 0-100%;
| 204C | Local_Upgrade_App_Status |  | U16 |  |  |  |  | R | App's current upgrade progress, high byte indicates upgrade status: 0x00: not in upgrade status; 0x01: being upgraded; 0x02: upgrade failed; 0x03: upgrade successful; Other: invalid; The low byte indicates the current upgrade progress: progress range 0-100%;
| 204D | Local_Upgrade_Arm_Status |  | U16 |  |  |  |  | R | ARM current upgrade progress, high byte indicates upgrade status: 0x00: not in upgrade status; 0x01: being upgraded; 0x02: upgrade failed; 0x03: upgrade successful; Other: invalid; The low byte indicates the current upgrade progress: progress range 0-100%;
| 204E | Local_Upgrade_Mdsp_Status |  | U16 |  |  |  |  | R | The current upgrade progress of the main DSP, the high byte indicates the upgrade status: 0x00: not in upgrade status; 0x01: being upgraded; 0x02: upgrade failed; 0x03: upgrade successful; Other: invalid; The low byte indicates the current upgrade progress: progress range 0-100%;
| 204F | Local_Upgrade_Sdsp_Status |  | U16 |  |  |  |  | R | The current upgrade progress of the sub-DSP, the high byte indicates the upgrade status: 0x00: not in upgrade status; 0x01: being upgraded; 0x02: upgrade failed; 0x03: upgrade successful; Other: invalid; The low byte indicates the current upgrade progress: progress range 0-100%;
| 2050 | Local_Upgrade_Bms_Status |  | U16 |  |  |  |  | R | BMS current upgrade progress, high byte indicates upgrade status: 0x00: not in upgrade status; 0x01: being upgraded; 0x02: upgrade failed; 0x03: upgrade successful; Other: invalid; The low byte indicates the current upgrade progress: progress range 0-100%;
| 2051 | Local_Upgrade_Fuse_Status |  | U16 |  |  |  |  | R | FUSE current upgrade progress, high byte indicates upgrade status: 0x00: not in upgrade status; 0x01: being upgraded; 0x02: upgrade failed; 0x03: upgrade successful; Other: invalid; The low byte indicates the current upgrade progress: progress range 0-100%;
| 2052 | Local_Upgrade_Pcu_Status |  | U16 |  |  |  |  | R | PCU current upgrade progress, high byte indicates upgrade status: 0x00: not in upgrade status; 0x01: being upgraded; 0x02: upgrade failure; 0x03: upgrade successful; Other: invalid; The low byte indicates the current upgrade progress: progress range 0-100%;
| 2053 | Local_Upgrade_Bdu_Status |  | U16 |  |  |  |  | R | BDU current upgrade progress, high byte indicates upgrade status: 0x00: not in upgrade status; 0x01: being upgraded; 0x02: upgrade failure; 0x03: upgrade successful; Other: invalid; The low byte indicates the current upgrade progress: progress range 0-100%;
| 2054 | Local_Upgrade_DcDcArm_Status |  | U16 |  |  |  |  | R | DC/DC ARM current upgrade progress, high byte indicates upgrade status: 0x00: not in upgrade status; 0x01: being upgraded; 0x02: upgrade failed; 0x03: upgrade successful; Other: invalid; The low byte indicates the current upgrade progress: progress range 0-100%;
| 2055 | Local_Upgrade_DcDcDsp_Status |  | U16 |  |  |  |  | R | DC/DC DSP current upgrade progress, high byte indicates upgrade status: 0x00: not in upgrade status; 0x01: being upgraded; 0x02: upgrade failed; 0x03: upgrade successful; Other: invalid; The low byte indicates the current upgrade progress: progress range 0-100%;
| 2056 | Local_Upgrade_Afci_Status |  | U16 |  |  |  |  | R | AFCI's current upgrade progress, the high byte indicates the upgrade status: 0x00: not in upgrade status; 0x01: being upgraded; 0x02: upgrade failed; 0x03: upgrade successful; Other: invalid; The low byte indicates the current upgrade progress: progress range 0-100%;
| 2057 -- 2087 | [8 empty] | Reserved as a supplement for subsequent different chip roles
VI. Compatible Shared Data Area (0x4E20-0x4FFF) |  |  | Shared data area (reserved)
Version of the agreement in force | 4E20 | VersionType |  | U16 |  |  | 0 | 1 | RW | Version of the protocol in force: 0: Generation 3 MODBUS. 1: Generation 4 MODBUS;
Intelligent Address Assignment | 4E21 | AutoAssignmentCtrl |  | U16 |  |  |  |  | RW | Encoded by bit, returns 0 when read without special instructions: bit0-trigger intelligent address assignment function, clear zero at the end of the process, return 1 when reading to indicate that the process is in progress; Other reserved.
| 4E22 | BroadcastGetSN |  | U16 |  |  |  |  | W | This register exists only when broadcasting a write and can be answered, and is issued in combination with the "Maximum Random Answer Time" below. High Byte. bit0~3 - indicates round 0-15, when it is 0, it will end the bit4 limit setting time immediately, and this command can take effect immediately, that is to say, when bit4 is set at the same time, it will trigger the function of bit4 and re-enter the limiting time; bit4-broadcast allow answering flag, after this flag is set to 1, there will be a restriction of setting again, the restriction time is 10 times the maximum random answering time, it can be carried out by the 0 value of bit0~3 to end this restriction time immediately, and clearing zero is no restriction; Other reserved. Low byte: Reserved.
| 4E23 | Broadcast Level |  | U16 |  | unit of angle or arc equivalent one sixtieth of a degree |  |  | W | Maximum random answer time
| 4E24 | ResponseLevel |  | U16 |  |  |  |  | RW | High byte: bit0 - broadcast allow answer flag, this bit can only be cleared here; Otherwise reserved; Low byte: reserved; (When issued with the following modbus address and sequence number, and for broadcast, compare whether the sequence number is a native message and is required to take effect and answer).
| 4E25 | AddrAndSnLen |  | U16 |  |  |  |  | RW | High byte - slave modbus address; Low byte - length of the sequence number; (This register needs to be sent with the following sequence number contents, and the broadcast write compares the sequence number to whether it is a native message and needs to be valid and answered).
| 4E26 -- 4E34 | SN1-SN15 |  | U16 |  |  |  |  | RW | Maximum30bytes of serial number content
VII. DCDC Data Area (0x5000-0x5FFF) |  |  | DC/DC Data
DCDC system information | 5000 -- 5003 | reserved | dcdc system information mask | U64 |  |  |  |  | R | reservations
| 5004 | RS485_modbus_version | ARM to Inverter 485 Protocol Version | U16 |  |  |  |  | R | e.g. 0x108
| 5005 | Rsvd0 | reserve | U16 |  |  |  |  | R | e.g. 0x108
| 5006 | Arm_SCI_protocol_version | ARM to DSP internal protocol version | U16 |  |  |  |  | R | e.g. 0x108
| 5007 | Dsp_SCI_protocol_version | DSP to ARM internal protocol version | U16 |  |  |  |  | R | e.g. 0x108
| 5008 | Arm_CAN_protocol_version | ARM to BMS CAN protocol version | U16 |  |  |  |  | R | e.g. 0x108
| 5009 | Rsvd1 | reserve | U16 |  |  |  |  | R | e.g. 0x108
| 500A | Dcdc_comm_protocol_version | DCDC Intermodule Protocol Version | U16 |  |  |  |  | R | e.g. 0x108
| 500B -- 500E | ARM_APP_Version | ARM app software version | ASCII |  |  |  |  | R | 8 bytes, occupies 4 registers. The high 8 bits of each register store the high digit, the low 8 bits store the low digit. For example, version number "V1.2.3-SF.RC1", register value:0x5346 0x2E52 0x4331 0x0000 According to the new version number rule major_version.minor_version.stage_version Special version: client_type.spec_version client_type takes 4 bytes, spec_version takes 4 bytes.
| 500F -- 5010 | CTRL_BD_HW_Version | Control Board Hardware Version | ASCII |  |  |  |  | R | 4 ASCII codes occupy 2 registers. The high 8 bits of each register hold the high digits, and the low 8 bits hold the low digits. For example, version number "V101", register value: 0x5631 3031
| 5011 -- 5014 | ARM_boot_Version | ARM bootloader software version | ASCII |  |  |  |  | R | 8 bytes, occupies 4 registers. The high 8 bits of each register store the high digit, the low 8 bits store the low digit. For example, version number "V1.2.3-SF.RC1", register value: 0x5346 0x2E52 0x4331 0x0000, that is, the string "SF.RC1". Follow the new version numbering rules major_version.minor_version.stage_version special version: client_type.spec_version
| 5015 | ARM_chip_code | ARM Chip Code | ASCII |  |  |  |  | R | 2 ASCII codes occupy 1 register. The high 8 bits of each register hold the high digit, the low 8 bits hold the low digit. Example: 0x4730 means "G0".
| 5016 -- 5019 | DSP_APP_version | DSP app software version | ASCII |  |  |  |  | R | 8 bytes, occupies 4 registers. The high 8 bits of each register store the high digit, the low 8 bits store the low digit. For example, version number "V1.2.3-SF.RC1", register value: 0x5346 0x2E52 0x4331 0x0000, that is, the string "SF.RC1". Follow the new version numbering rules major_version.minor_version.stage_version special version: client_type.spec_version
| 501A -- 501B | POWER_BD_HW_version | Power Board Hardware Version | ASCII |  |  |  |  | R | 4 ASCII codes occupy 2 registers. The high 8 bits of each register hold the high digits, and the low 8 bits hold the low digits. For example, version number "V101", register value: 0x5631 3031
| 501C -- 501F | DSP_boot_version | DSP bootloader software version | ASCII |  |  |  |  | R | 8 bytes, occupies 4 registers. The high 8 bits of each register store the high digit, the low 8 bits store the low digit. For example, version number "V1.2.3-SF.RC1", register value: 0x5346 0x2E52 0x4331 0x0000, that is, the string "SF.RC1". Follow the new version numbering rules major_version.minor_version.stage_version special version: client_type.spec_version
| 5020 | DSP_chip_code | DSP Chip Code | ASCII |  |  |  |  | R | 2 ASCII codes occupy 1 register. The high 8 bits of each register hold the high digit, the low 8 bits hold the low digit. Example: 0x4730 means "G0".
| 5021 -- 5022 | ARM_APP_version_add | ARM APP version number supplement | U16 |  |  |  |  | R | 2 registers, according to the new version number rule major_version.minor_version.stage_version For example, version number "V1.2.3-SF.RC1", register value: 0x0001 0x0203
| 5023 -- 5024 | ARM_boot_version_add | ARM BOOT version number supplement | U16 |  |  |  |  | R | 2 registers, according to the new version number rule major_version.minor_version.stage_version For example, version number "V1.2.3-SF.RC1", register value: 0x0001 0x0203
| 5025 -- 5026 | DSP_APP_version_add | DSP APP version number supplement | U16 |  |  |  |  | R | 2 registers, according to the new version number rule major_version.minor_version.stage_version For example, version number "V1.2.3-SF.RC1", register value: 0x0001 0x0203
| 5027 -- 5028 | DSP_boot_version_add | DSP BOOT version number supplement | U16 |  |  |  |  | R | 2 registers, according to the new version number rule major_version.minor_version.stage_version For example, version number "V1.2.3-SF.RC1", register value: 0x0001 0x0203
| 5029 -- 5032 | serial_No | Device SN number | ASCII |  |  |  |  | R | 20 ASCII codes, occupying 10 registers. The high 8 bits of each register store the high digit, the low 8 bits store the low digit. For example, SN number "SD1021080KC223140001".
| 5033 -- 5038 | serial_No_rvsd | Device SN number reservation | ASCII |  |  |  |  | R | 12 ASCII code reservations, occupying 6 registers.
| 5039 -- 503F | rsvd | reserve | U16 |  |  |  |  | R | 7 registers reserved
DCDC real-time data | 5040 -- 5043 | reserved | DCDC real-time data mask | U64 |  |  |  |  | R | reservations
| 5044 | parall_dcdc_num | Total number of current parallel DCDC modules | U16 |  |  | 1 | 4 | R
| 5045 | start_time_countdown | countdown | U16 |  | second | 0 |  | R
| 5046 | dcdc_run_state | DCDC system operational status | U16 |  |  |  |  | R | 0-Standby; 1-Discharge; 2-Charge
| 5047 | load_derating_reason | power limiting state | U16 |  |  |  |  | R | 0-Unlimited power; 1-Command limited work; 2-Soc limiting work; 3-Over-temperature limiting work; 4-Boost ratio load shedding; 5-Overvoltage load shedding on the high voltage side; 6-Fan failure load shedding;
| 5048 | soc_power_ration | Percentage of SOC equalized power | I16 | 0.1 | % | -1000 | 1000 | R | Read-only for the external network, calculated and set by the host for the internal network
| 5049 | DSP_state | DSP working status | U16 |  |  |  |  | R | 0-Wait Wait 1-Check Check 2-Normal Normal operation 3-RecoverFault Recoverable fault 4-PermenentFault PermanentFault
| 504A | fan_outside_maxspeed | Maximum speed of external fan | U16 |  |  |  |  | R
| 504B | fan_outside_speed | Actual speed of external fan | U16 |  |  | 0 | 3 | R
| 504C | fan_inside_maxspeed | Maximum internal fan speed | U16 |  |  |  |  | R
| 504D | fan_inside_speed | Actual internal fan speed | U16 |  |  | 0 | 3 | R
| 504E | low_bus_volt | Low voltage side bus voltage | I16 | 0.1 | V |  |  | R
| 504F | low_bus_volt_pre | Low voltage side relay front end voltage | I16 | 0.1 | V |  |  | R
| 5050 | rsvd | Low voltage side current | I16 | 0.1 | A |  |  | R
| 5051 | low_bus_power | Low voltage side power | I16 | 0.01 | kw |  |  | R
| 5052 | low_bus_curr_total | Total current on the low voltage side | I16 | 0.1 | A |  |  | R
| 5053 | branch_num | Number of parallel branches | U16 |  |  |  |  | R
| 5054-5057 | branch_curr1-4 | Branch1-4current | I16 | 0.1 | A |  |  | R
| 5058-505B | branch_flycap_volt1-4 | Branch1-4fly across capacitor voltage | I16 | 0.1 | V |  |  | R
| 505C | high_bus_volt | High voltage busbar voltage | I16 | 0.1 | V |  |  | R
| 505D | high_bus_volt_pre | Voltage at front end of relay on high voltage side | I16 | 0.1 | V |  |  | R
| 505E | iso_res | Insulation impedance | U16 |  | kΩ |  |  | R
| 505F | auxiliary_volt | 12V auxiliary voltage | U16 | 0.1 | V |  |  | R
| 5060 | inner_temp | Chassis internal ambient temperature | I16 | 1 | ℃ |  |  | R
| 5061 | radiator_temp1 | Radiator temperature 1 | I16 | 1 | ℃ |  |  | R
| 5062 | radiator_temp2 | Radiator temperature 2 | I16 | 1 | ℃ |  |  | R
| 5063 | rvsd_temp1 | temperature reservation | I16 |  |  |  |  | R
| 5064 | rvsd_temp2 | temperature reservation | I16 |  |  |  |  | R
| 5065 -- 506E | fault_word1-10 | Faulty words1-10 | U16 |  |  |  |  | R | 10 addresses with fault IDs starting at 1 and ranging from 1-160
| 506F -- 5073 | state_word1-5 | status word | U16 |  |  |  |  | R | 5 addresses, BIT0: arm reset; cleared after inverter writes grid-connected parameters or real-time control
| 5074 -- 5075 | charge_energy | charge | U32 | 1 | Wh |  |  | R
| 5076 -- 5077 | discharge_energy | electrical discharge | U32 | 1 | Wh |  |  | R
| 5078 -- 507F | rvsd | reserve | U16 |  |  |  |  | R | 8 addresses reserved
| 5080 -- 5083 | reserved | DCDC system parameter mask | U64 |  |  |  |  | R | reservations
time setting | 5084 | systemtime_year | System time - years | U16 |  |  | 0 | 99 | RW | 2000 as a baseline | [7 empty] | Supportswritingfrom5084only,6addressesin a row
| 5085 | systemtime_month | System time-months | U16 |  |  | 1 | 12 | RW
| 5086 | systemtime_date | System time - day | U16 |  |  | 1 | 31 | RW
| 5087 | systemtime_hour | System time - hour | U16 |  |  | 0 | 23 | RW
| 5088 | systemtime_minute | System time - minutes | U16 |  |  | 0 | 59 | RW
| 5089 | systemtime_second | System Time-Second | U16 |  |  | 0 | 59 | RW
485 Communication Settings | 508A | RS485_address | RS485 external network address | U16 |  |  | 1 | 247 | RW | [8 empty] | Supportswritingfrom508Aonly, 4 addresses in a row
| 508B | external_net_485_baud | RS485 external network baud rate | U16 |  |  |  |  | RW | RS485 baud rate selection;0: 1200bps (not supported) 1: 2400bps 2: 4800bps 3: 9600bps (default) 4: 19200bps 5: 38400bps 6: 57600bps 7: 115200bps
| 508C | external_net_485_stopbit | RS485 external network stop bit | U16 |  |  |  |  | RW | RS485 stop bit selection; 0: 1 bit stop bit (default)1: 1.5-bit stop bit (not supported) 2: 2-bit stop bit
| 508D | external_net_485_checkbit | RS485 external network parity bit | U16 |  |  |  |  | RW | RS485 parity bit selection; 0: No checksum/None (default) 1: Even parity/Even 2: Odd parity/Odd3: High/Mark (not supported) 4: Low/Space (not supported)
Restore Factory Settings | 508E | reset_flag | Restore Factory Settings Security Flag | U16 |  |  |  |  | RW | Write to 0xDCDC to take effect; others are invalid | [7 empty] | Supportswritingfrom508Eonly,2addressesin a row
| 508F | factory_reset | Restore Factory Settings | U16 |  |  |  |  | RW | Restores the factory register; Bit value of 1 is valid. Bit0: Reserved Bit1: clear event log Bit2: Restore default values for all function configuration parameters When reading, return to the status of the last write operation: 0x0000: Success 0x0001-0x00FF: operation in progress
| 5090 -- 50BF | rsvd | reserve | U16 | [5 empty] | 48 addresses reserved
| 50C0-50C3 | reserved | DCDC factory set mask | U64 |  |  |  |  | R | reservations
Serial Number Setting | 50C4-50CD | device_sn | Device SN number | ASCII |  |  |  |  | RW | 20 ASCII codes, occupying 10 registers. The high 8 bits of each register store the high digit, the low 8 bits store the low digit. For example, SN number "SD1021080KC223140001". | [7 empty] | Supportswritingfrom50C4only,10addressesin a row
| 50CE-50D3 | device_sn_rvsd | Device SN number reservation | ASCII |  |  |  |  | RW | 12 ASCII code reservations, occupying 6 registers.
factory model | 50D4 | factory_mode | Factory mode control | U16 |  |  |  |  | RW | Factory Mode-State Control. Bit0: Factory mode enable bit Bit1: T1 completion flag Bit2: Aging completion flag Bit3: T2 completion flag Bit4: Packaging test completion flag | [7 empty] | Supports address range, 1-n register writes
| 50D5 | factory_privilege | Factory Pattern Privileges | U16 |  |  |  |  | RW | Factory Pattern - Privilege Control. Privilege control write 0 is invalid, write 1 is valid. Bit0: clear calibration coefficients Bit1: Clear the DCDC event record Bit2: Clear PCU event log On read, returns the status of the last write operation: Bit 0: Success Bit 1: Operation in progress
| 50D6 | discharge_power_ratio | Percentage of discharge power | U16 |  | % | 0 | 100 | RW
| 50D7 | charge_power_ratio | Percentage of charging power | U16 |  | % | 0 | 100 | RW
| 50D8 | branch1_ctrl_word | Channel 1 control word | U16 |  |  |  |  | RW | 0-Standby; 1-Discharge; 2-Charge
| 50D9 | branch2_ctrl_word | Channel 2 Control Word | U16 |  |  |  |  | RW | 0-Standby; 1-Discharge; 2-Charge
| 50DA | branch3_ctrl_word | Channel 3 Control Word | U16 |  |  |  |  | RW | 0-Standby; 1-Discharge; 2-Charge
| 50DB | branch4_ctrl_word | Channel 4 Control Word | U16 |  |  |  |  | RW | 0-Standby; 1-Discharge; 2-Charge
| 50DC | flycap1_fix_ctrl_word | Fly across capacitor 1 calibration control | U16 |  |  |  |  | RW | 01 - Flying across capacitor calibration control in effect, others not in effect
| 50DD | flycap2_fix_ctrl_word | Fly Span Capacitor 2 Calibration Control | U16 |  |  |  |  | RW | 01 - Flying across capacitor calibration control in effect, others not in effect
| 50DE | flycap3_fix_ctrl_word | Fly-Through Capacitor 3 Calibration Control | U16 |  |  |  |  | RW | 01 - Flying across capacitor calibration control in effect, others not in effect
| 50DF | flycap4_fix_ctrl_word | Fly Span Capacitor 4 Calibration Control | U16 |  |  |  |  | RW | 01 - Flying across capacitor calibration control in effect, others not in effect
| 50E0 - 50FF | rsvd | reserve | U16 |  |  |  |  | R | 32 reserved
| 5100 - 5103 | reserved | DCDC Calibration Parameter Mask | U64 |  |  |  |  | R | reservations
calibration parameters | 5104 | high_bus_asf | High Voltage Bus Voltage Scaling Factor | U16 | 0.001 |  | 950 | 1050 | RW | [8 empty] | Supports address range,1-nwrites
| 5105 | high_bus_offset | High Voltage Bus Voltage Offset | I16 | 0.1 | V | -150 | 150 | RW
| 5106 | low_bus_asf | Low-voltage side bus voltage scale factor | U16 | 0.001 |  | 950 | 1050 | RW
| 5107 | low_bus_offset | Low-voltage side bus voltage offset | I16 | 0.1 | V | -150 | 150 | RW
| 5108 | branch1_curr_asf | Branch 1 current scaling factor | U16 | 0.001 |  | 950 | 1050 | RW
| 5109 | branch1_curr_offset | Branch 1 current offset | I16 | 0.1 | A | -150 | 150 | RW
| 510A | flycap1_asf | Branch 1 fly across capacitor voltage scale factor | U16 | 0.001 |  | 950 | 1050 | RW
| 510B | flycap1_offset | Branch 1 fly across capacitor voltage offset | I16 | 0.1 | V | -150 | 150 | RW
| 510C | branch2_curr_asf | Branch 2 current scaling factor | U16 | 0.001 |  | 950 | 1050 | RW
| 510D | branch2_curr_offset | Branch 2 current offset | I16 | 0.1 | A | -150 | 150 | RW
| 510E | flycap2_asf | Branch 2 fly across capacitor voltage scaling factor | U16 | 0.001 |  | 950 | 1050 | RW
| 510F | flycap2_offset | Branch 2 fly across capacitor voltage offset | I16 | 0.1 | V | -150 | 150 | RW
| 5110 | branch3_curr_asf | Branch 3 current scaling factor | U16 | 0.001 |  | 950 | 1050 | RW
| 5111 | branch3_curr_offset | Branch 3 current offset | I16 | 0.1 | A | -150 | 150 | RW
| 5112 | flycap3_asf | Branch 3 fly across capacitor voltage scale factor | U16 | 0.001 |  | 950 | 1050 | RW
| 5113 | flycap3_offset | Branch 3 fly across capacitor voltage offset | I16 | 0.1 | V | -150 | 150 | RW
| 5114 | branch4_curr_asf | Branch 4 current scaling factor | U16 | 0.001 |  | 950 | 1050 | RW
| 5115 | branch4_curr_offset | Branch 4 current offset | I16 | 0.1 | A | -150 | 150 | RW
| 5116 | flycap4_asf | Branch 4 fly across capacitor voltage scaling factor | U16 | 0.001 |  | 950 | 1050 | RW
| 5117 | flycap4_offset | Branch 4 fly across capacitor voltage offset | I16 | 0.1 | V | -150 | 150 | RW
| 5118 | low_bus_pre_asf | Proportionality factor of the voltage at the front end of the relay on the low voltage side | U16 | 0.001 |  | 950 | 1050 | RW
| 5119 | low_bus_pre_offset | Voltage offset at the front end of the relay on the low-voltage side | I16 | 0.1 | V | -150 | 150 | RW
| 511A | high_bus_pre_asf | Proportionality coefficient of the voltage at the front end of the relay on the high voltage side | U16 | 0.001 |  | 950 | 1050 | RW
| 511B | high_bus_pre_offset | Voltage offset of the front end of the relay on the high voltage side | I16 | 0.1 | V | -150 | 150 | RW
| 511C - 513F | rsvd | reserve | U16 |  |  |  |  | R | 36 reserved
| 5140 - 5143 | reserved | DCDC control parameter mask | U64 |  |  |  |  | R | reservations
| 5144 | parral_dcdc_num_set | Parallel DCDC quantity setting | U16 |  |  | 1 | 4 | RW | Support manual configuration, the inverter sends a broadcast notification to all DCDCs, when the system is installed, according to how many DCDCs are connected to the hardware to set up, the number of DCDCs set up and the number of DCDCs actually online to compare, you can determine whether there is a DCDC dropped. | [7 empty] | Supports single-register writes only
| 5145 | dcdc_encoded | DCDC code | U16 |  |  | 0 | 3 | RW | Support the upper computer to access different DCDC data, reserved Maximum support for 4 groups in parallel, code 00~03, default stand-alone code is 00 | [7 empty] | Supports single-register writes only
Parameters for grid connection | 5146 | start_wait_time | boot-up waiting time | U16 | 1 | second | 0 |  | RW | [8 empty] | Supports address range, 1-10 register writes
| 5147 | grid_volt_normal | Rated grid voltage | U16 | 0.1 | V |  |  | RW
| 5148 | grid_frequnce_normal | Grid rated frequency | U16 | 0.01 | Hz |  |  | RW
| 5149 | grid_phase_num | Number of grid phases | U16 |  |  |  |  | RW | 1-single-phase; 3-three-phase
| 514A | leak_curr_limit | Leakage current protection value for calculation of insulation impedance | U16 | 1 | mA |  |  | RW
| 514B | rise_time | 0 power rise to rated power time | U16 | 1 | ms |  |  | RW
| 514C | fall_time | Rated power drop to 0 power time | U16 | 1 | ms |  |  | RW
| 514D | power_N_to_P_time | Charge/discharge power conversion time (90% charge/discharge conversion) | U16 | 1 | ms |  |  | RW
| 514E | charge_curr_max | Maximum allowable charging current | I16 | 0.1 | A |  |  | RW
| 514F | discharge_curr_max | Maximum permissible discharge current | I16 | 0.1 | A |  |  | RW
| 5150 - 515F | rsvd | 16 reserved | U16 |  |  |  |  | RW | 16 reserved
Real-time power control | 5160 | remote_onoff | Remote switch on/off | U16 |  |  |  |  | RW | Occupies 1 register 0x55-Power on; 0xAA-Power off | [7 empty] | Supports address range,1-8writes
| 5161 | force_off | forced switching | U16 |  |  |  |  | RW | Occupies 1 register 0x55-Power on; 0xAA-Power off
| 5162 | fan_derating_power_ratio | Percentage of fan power limit | U16 |  | % | 0 | 100 | RW | Reserved, occupies 1 register.
| 5163 | power_level | Model Power Rating | U16 |  |  |  |  | RW | Occupies 1 register 0x01-5KW; 0x05-25KW; other-reserved
| 5164 | discharge_charge_mode | Charge and Discharge Mode | U16 |  |  |  |  | RW | Occupies 1 register 0x0-Standby; 0x01-Autonomous charging and discharging; 2-Forced charging; 3-Forced discharging; Other invalid Support manual configuration
| 5165 | real_power_ctrl_en | Real-time power enable | U16 |  |  |  |  | RW | Occupies 1 register 0x55-enable; 0xAA-disable
| 5166 | real_power_ratio | Real-time output power percentage | U16 |  | % | 0 | 100 | RW | Charge/discharge power configuration with charge/discharge mode
| 5167 | discharge_charge_curr_ref | Charge and Discharge Current Command | U16 |  |  |  |  | RW | Charge/discharge current configuration with charge/discharge mode
| 5168 - 517E | rvsd1 | 23 reserved | U16 | [5 empty] | 23 reserved
Remove power | 517F | clear_energy | DCDC power count from 0 | U16 |  |  |  |  | RW | Clearing DCDC power statistics | [7 empty] | Supports single-register writes only
historical incident | 5180 - 530C | HistoryEventList_ID1-100 |  | U16 |  |  |  |  | R | Historical event ID most recent 1-100th; interval is 4 registers | [7 empty] | Supports onlymultiples4
| 5181 - 530D | HistoryEventList_yM1-100 |  | U16 |  |  |  |  | R | High byte: the two lower digits of the year decimal number; Low byte: month. The interval is 4 registers
| 5182 - 530E | HistoryEventList_dH1-100 |  | U16 |  |  |  |  | R | High byte: date; Low byte: hour. Interval is 4 registers
| 5183 - 530F | HistoryEventList_ms1-100 |  | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds. Interval is 4 registers
| 5340 - 5343 | reserved | DCDC debug data setup mask | U64 |  |  |  |  | R | reservations
Recorded Wave Object Settings | 5344 - 5358 | remote_test_ctr_word 1-5 | Remote Debugging Control Word 1-5 | U16 |  |  |  |  | RW | The high byte indicates debug object selection: 0: communication board; 1: control board 1 (main DSP); 2: Control board 2 (secondary DSP); 3: Fuse; The low byte indicates the item number: 0-255 | [7 empty] | Onlymultiples5starting5344,supportedfor writing
| 5345 - 5359 | remote_test_data_addr 1-5 | Data addresses 1-5 | U32 |  |  |  |  | RW
5346 - 535A
| 5347 - 535B | remote_test_data_asf 1-5 | Magnification 1-5 | U16 |  |  |  |  | RW | The magnification is 10^N and N is the value of the register. Used for floating point data take out.
| 5348 - 535C | remote_test_data_type 1-5 | Data types 1-5 | U16 |  |  |  |  | RW | 0: 16-bit integer 1 or other: 32-bit floating point
| 535D - 535E | rsvd[3] | 3 retained | U16 |  |  |  |  | R
Recorded Wave Read Configuration | 535F | remote_test_read_word0 |  | U16 |  |  |  |  | RW | High byte: reserved Low byte: read the first recording data; 0 means the most recent one; 1 means the second most recent recording data, and so on. | [7 empty] | Supports address range,1-3writes
| 5360 | remote_test_read_word1 | Remote Debugging-Read Configuration Word 1 | U16 |  |  |  |  | RW | The high byte indicates debug object selection:0: communication board;1: control board1(mainDSP);2Control board2(secondaryDSP);3:Fuse; The low byte indicates the item number:0-255
| 5361 | remote_test_read_word2 | Remote Debugging-Read Configuration Word 2 | U16 |  |  |  |  | RW | Read data start offset
| 5362 | remote_test_force_str | Remote Debugging - Force Trigger | U16 |  |  |  |  | W | 0x01: Force trigger enable 0x00: Force trigger disable | [7 empty] | Supports single-register writes only
| 5363 | remote_test_hookup | Remote Debugging - Trigger Hang | U16 |  |  |  |  | W | 0x01: Trigger hang 0x00: trigger normal | [7 empty] | Supports single-register writes only
| 5364 | remote_arm_reset | Remote Reset ARM | U16 |  |  |  |  | W | 1-ARM reset | [7 empty] | Supports single-register writes only
| 5365 - 537F | rvsd1 | Retained 27 | U16 |  |  |  |  | R
Recorded waveform data reading | 5380 | year |  | U16 |  |  |  |  | R | 0x07E7 indicates 2023; fault recording time
| 5381 | mon_date |  | U16 |  |  |  |  | R | High byte indicates month 1-12 Low byte indicates days 1-31
| 5382 | hour_min |  | U16 |  |  |  |  | R | High byte indicates hours 0-59 Low byte indicates minutes 0-59
| 5383 | sec_obj |  | U16 |  |  |  |  | R | High byte indicates seconds 0-59 Low byte - reserved
| 5384 - 53BF | remote_test_data[60] | Remote commissioning data 1-60 | I16 |  |  |  |  | R | recorded waveform data
| 53C0-53C3 | reserved | DCDC Administrator Control Mask | U64 |  |  |  |  | R | reservations
Protect Enable | 53C4-53CD | protect_en[10] | Fail-safe enable 1-10 | U16 |  |  |  |  | RW | Each bit corresponds to a fault, refer to the fault resolution. 1: enable protection (enable this function) 0: Do not enable | [7 empty] | Supports address range, 1-10 register writes
Alarm Enable | 53CE-53D7 | alarm_en[10] | Fault Alarm Enable 1-10 | U16 |  |  |  |  | RW | Each bit corresponds to a fault, refer to the fault resolution. 1: alarm enabled (displayed externally) 0: not enable (no external display) | [7 empty] | Supports address range,1-10writes
Setting the address | 53D8 | LogicAddr |  | U16 |  |  | 1 | 4 | RW | Manually set the logical address, so you can manually assign it when the automatic assignment conflicts | [7 empty] | Supports only 2 register concatenation starting at 53D8
| 53D9 | MacAddr |  | U16 |  |  | 0 | 255 | RW | Manually set the MAC address, which can be assigned manually when there is a conflict with automatic assignment
Strobe Light Positioning | 53DA | LedFlash |  | U16 |  | second | 0 | 60 | RW | The DCDC receives this command and flashes the light quickly to easily locate which machine it is; the parameter is the flash time | [7 empty] | Supports single-register writes only
Administrator Control Word | 53DB | AdminCtrl |  | U16 |  |  |  |  | RW | bit0: Write 1 to clear permanent faults (permanent faults need to be artificially cleared when a permanent fault occurs in the DSP;) Other bits are temporarily reserved | [7 empty] | Supports single-register writes only
| 53DC-53FF | rsvd | Reserve 40. | U16 |  |  |  |  | R
parallel address table | 5400 | dcdc_count | Number of DCDCs online | U16 |  |  | 1 | 4 | R
| 5401-5403 | rsvd1[3] | 3 retained | U16 |  |  |  |  | R
| 5404-5416 | mac_addr1-4 | physical address | U64 |  |  |  |  | R | Devices 1-4, spaced 6 addresses apart
| 5405-5417 | [8 empty] | Devices 1-4, spaced 6 addresses apart
| 5406-5418 | [8 empty] | Devices 1-4, spaced 6 addresses apart
| 5407-5419 | [8 empty] | Devices 1-4, spaced 6 addresses apart
| 5408-541A | rs485_addr1-4 | RS485 address | U16 |  |  | 1 | 247 | R | Devices 1-4, spaced 6 addresses apart
| 5409-541B | logic_addr1-4 | logical address (computing) | U16 |  |  | 1 | 4 | R | Devices 1-4, spaced 6 addresses apart
| 541C-543F | rsvd2 | Retention of 36 | U16 |  |  |  |  | R | Reserved addresses for 6 devices
VIII. PCU &amp; BDU data area (0x6000-0x6FFF) |  |  | PCU and BDU data
| 6000 -- 6003 | AddressMask_PCU1 |  | U64 |  |  |  |  | R | Mask area for the 64 register address words starting at this address. Refer to the description of address 0x0040 |  | 0 | 0000000F
| 6004 | PCU_Number | [6 empty] | R | Total number of PCUs online.
| 6005 -- 600F | [7 empty] | R | Aggregate information set-aside (11)
| 6010 | PCU_ID |  | U16 |  |  |  |  | R | PCU number. | [7 empty] | The number of each PCU in the multicomputer system, with the numbering starting from 1.
| 6011 -- 601A | PCU_SN0 -- 9 |  | ASCII |  |  |  |  | R | PCU serial numbers 0-9 (10) | [7 empty] | PCU finished serial number, ASCII code form, please check 0x6011 address description for case. Example:0x5043 stands for "PC".
| 601B -- 601C | PCU_Software_Version1 -- 2 |  | ASCII |  |  |  |  | R | Software version numbers 1-2 | [7 empty] | PCU version information, e.g.: software version V010012, hardware version: 0200, CAN protocol version: 0102
| 601D | PCU_Hardware_Version |  | U16 |  |  |  |  | R | Hardware version number
| 601E | PCU_Can1_Version |  | U16 |  |  |  |  | R | CAN1 protocol version number
| 601F | PCU_Can2_Version |  | U16 |  |  |  |  | R | CAN2 protocol version number
| 6020 | PCU_Work_State |  | U16 |  |  |  |  | R | Module Status 0: Update 1: Check 2: Normal 3：Active 4: Fault 5: Permanent Fault | [7 empty] | Update:Software upgrade status Check:Self-checking state, PCU initial state Normal:Normal charging/discharging operation state Active:Active BMS status. Fault:Recoverable Fault status, the fault can be recovered by reaching specific conditions. Permanent Fault:Permanent fault state, not recoverable.
| 6021 | PCU_Internal_Temperature |  | U16 | 1 | ℃ |  |  | R | Chassis internal temperature | [7 empty] | Example: 0x0001 means that the temperature 1 in the chassis is 1°C
| 6022 | PCU_Radiator_Temperature1 |  | I16 | 1 | ℃ |  |  | R | Radiator 1 temperature | [7 empty] | Example: 0x0001 means that the radiator temperature 1 is 1°C
| 6023 | PCU_Radiator_Temperature2 |  | I16 | 1 | ℃ |  |  | R | Radiator 2 temperature (reserved, not used)
| 6024 -- 6027 | PCU_Warning1 -- 4 |  | U16 |  |  |  |  | R | Warning 1-4 Example: 0x4000 means no discharge warning | [7 empty] | Record PCU fault information, corresponding fault information see "PCU Fault Bit Description", please refer to 0x6024 address description for case study.
| 6028 -- 602B | PCU_Fault1 -- 4 |  | U16 |  |  |  |  | R | Fault 1-4 Example: 0x0001 means radiator over temperature protection
| 602C | PCU_DC_High_Voltage |  | U16 | 0.1 | V | 0 |  | R | DC High Side Voltage | [7 empty] | PCU high voltage side voltage, example:0x0FD3 represents 405.1V
| 602D | PCU_DC_Low_Voltage |  | U16 | 0.1 | V | 0 |  | R | DC Low Side Voltage | [7 empty] | Low voltage battery voltage, example:0x0214 represents 53.2V
| 602E | PCU_Low_Current |  | I16 | 0.1 | A |  |  | R | DC low voltage side current | [7 empty] | Low voltage battery current, charging is positive, discharging is negative. Example:0xFFAF means discharge 5.1A.
| 602F | PCU_Low_Power |  | I16 | 0.01 | kW |  |  | R | DC Low Side Power | [7 empty] | Low-voltage battery output power, charging is positive, discharging is negative Example:0x0F8C5 means discharge 1851W.
| 6030 | PCU_BusP |  | U16 | 0.1 | V |  |  | R | Positive bus voltage | [7 empty] | unused
| 6031 | PCU_BusN |  | U16 | 0.1 | V |  |  | R | Negative bus voltage
| 6032 -- 6035 | PCU_FC_Voltage1 -- 4 |  | U16 | 0.1 | V |  |  | R | Fly across capacitor voltage 1-4
| 6036 -- 6039 | PCU_IL_Current1 -- 4 |  | I16 | 0.1 | A |  |  | R | Inductive current branch 1-4
| 603A -- 603F | [8 empty] | reserve
| 6040 -- 6043 | AddressMask_PCU2 |  | U64 |  |  |  |  | R | Mask area for the 64 register address words starting at this address. Refer to the description of address 0x0040 |  | 0 | 0000000F
| 6044 | PCU_Inquire |  | U16 |  |  | 1 | 32 | RW | PCU Query Control Word. Select the PCU module to be read or set by setting this register. | [7 empty] | This control word is used to query the PCU module of a specific number
| 6045 | PCU_Remote_On_Off |  | U16 |  |  | 0 | 3 | RW | DC Module Remote Switch On/Off 0: Shutdown 1: Prohibit charging 2: Discharge prohibited 3: Charging and discharging allowed | [7 empty] | unused
| 6046 | PCU_Max_Charge_Current |  | U16 | 0.1 | A | 0 | 65535 | RW | Maximum charging current of DC module | [7 empty] | unused
| 6047 | PCU_Max_Discharge_Current |  | U16 | 0.1 | A | 0 | 65535 | RW | Maximum discharge current of DC module
| 6048 | K_Voltage_HVbus |  | U16 | 0.001 | p.u. | 950 | 1050 | RW | HV side hvbus voltage calibration ratio Example:0x03D5 represents 0.981 | [7 empty] | Used to calibrate PCU sample values, see 0x6048 address description for cases
| 6049 | K_Voltage_Pbus |  | U16 | 0.001 | p.u. | 950 | 1050 | RW | HV side pbus voltage calibration ratio
| 604A | K_Current_HV_Chg |  | U16 | 0.001 | p.u. | 950 | 1050 | RW | HV side charging current calibration ratio
| 604B | K_Current_HV_Dchg |  | U16 | 0.001 | p.u. | 950 | 1050 | RW | HV side discharge current calibration ratio
| 604C | K_Voltage_LV |  | U16 | 0.001 | p.u. | 950 | 1050 | RW | Low voltage side voltage calibration ratio
| 604D | K_Current_LV_Chg |  | U16 | 0.001 | p.u. | 950 | 1050 | RW | Low voltage side charging current calibration ratio
| 604E | K_Current_LV_Dchg |  | U16 | 0.001 | p.u. | 950 | 1050 | RW | Low voltage side discharge current calibration ratio
| 604F -- 607F | [8 empty] | reserve
| 6080 -- 6083 | AddressMask_BDU1 |  | U64 |  |  |  |  | R | Mask area for the 64 register address words starting at this address. Refer to the description of address 0x0040 |  | 0 | 0000000F
BDU Information | 6084 | BDU_Number |  | U16 |  |  |  |  | R | Total number of BDUs online.
| 6085 -- 608F | [7 empty] | R | Aggregate information set-aside (11)
| 6090 | BDU_ID |  | U16 |  |  |  |  | R | BDU numbering. The numbering starts from 1.
| 6091 -- 609A | BDU_SN0 -- 9 |  | ASCII |  |  |  |  | R | BDU serial numbers 0-9 (10)
| 609B | Software_Version_Stage_BDU |  | ASCII |  |  |  |  | R | BDU chip software version number stage definition bits. The lower 8 bits of the register hold the ASCII code. The default value for the official version is 'V'.
| 609C | Software_Version_Major_BDU |  | ASCII |  |  |  |  | R | BDU chip software master version number. All chip master version numbers in the same system must be the same, otherwise it is considered as a system failure. The high 8 bits of the register store the high digit; The lower 8 bits of the register store the low digit.
| 609D | Software_Version_Custom_BDU |  | ASCII |  |  |  |  | R | BDU chip software non-standard customized version number. The version number of the standard software is "00". The non-standard customized version number of all chips in the same system must be the same, otherwise it is regarded as a system failure. The high 8 bits of the register store the high digits; The lower 8 bits of the register store the lower digits.
| 609E | Software_Version_Minor_BDU |  | ASCII |  |  |  |  | R | BDU chip software subversion number. The high 8 bits of the register store the high digit; The low 8 bits of the register store the low digit.
| 609F | BDU_Fault1 |  | U16 |  |  |  |  | R | BDU fault message 1
| 60A0 | BDU_Battery_Number |  | U16 |  |  |  |  | R | Number of cells per cluster
| 60A1 | TotalNum_PV |  | U16 | 1 |  |  |  | R | Total number of strings
| 60A2 | TotalNum_Battery |  | U16 | 1 |  |  |  | R | Total number of battery circuits
| 60A3 -- 60BF | [8 empty] | reserve
| 60C0 -- 60C3 | AddressMask_BDU2 |  | U64 |  |  |  |  | R | Mask area for the 64 register address words starting at this address. Refer to the description of address 0x0040 |  | 0 | 0000000F
| 60C4 | BDU_Inquire |  | U16 |  |  | 1 |  | RW | BDU Query Control Word. Select the BDU module to be read or set by setting this register.
| 60C5 | RatedPower_N_ID |  | U16 | 1 |  | 255 |  | RW | Operate the number of the specified path, within the total number of paths in the string, starting from 1.
| 60C6 | RatedPower_N_PV |  | U16 | 1 |  |  |  | R | String power rating for the specified number of circuits
| 60C7 | RatedPower_N_Battery |  | U16 | 1 |  |  |  | R | Battery rating for the specified number of circuits
| 60AC-61FF | [8 empty] | reserve
X. Meter information area (0x7080-0x70FF) |  |  | Customize serial number and model
Meter type automatic Recognition status | 7080 | MeterAutoIdentificationstate |  | U16 |  |  | 0 | 2 | R | Meter type auto-recognition status: bit0-3, status. 0 - automatic meter type recognition not activated; 1 - meter type automatic recognition in progress; 2 - meter type automatic identification successful; 3 - meter type automatic identification failed; Other - reserved; bit4-15 meter type: Reserved; | installer
Number of meters | 7081 | MeterConnectNum |  | U16 |  |  | 0 | 65535 | R | Number of external system meters
XII. BMS Transmission Area (0x9000-0x9FFF) |  |  | BMS Message Transmission
| 9000 -- 9003 | AddressMask_BMS1_System |  | U64 |  |  |  |  | R | Mask area for the 64 register address words starting at this address. Refer to the description of address 0x0040 |  | 0 | 0000000F
BMS Basic Information | 9004 | BMS_Sys_Time |  | U32 |  |  |  |  | R | BMS System Clock Bit0-5: second, range 0-59 Bit6-11: minute, range 0-59 Bit12-16: hour, range 0-23 Bit17-21: day, range 1-31 Bit22-25: month, range 1-12 Bit26-31: year, range 0-63 (starting from 2000)
9005
| 9006 | BMS_CAN_Version |  | U16 |  |  |  |  | R | CAN protocol version number
| 9007 | BMS_Manufacture_Name0 |  | U16 |  |  |  |  | R | Vendor Information 0 Example:0x414D stands for "AM".
| 9008 -- 900A | BMS_Manufacture_Name1 -- 3 |  | U16 |  |  |  |  | R | Manufacturer Information 1-3
| 900B | BMS_Version |  | U16 |  |  |  |  | R | BMS version number
| 900C | Cell_Type |  | U16 |  |  |  |  | R | Cell Type
| 900D | BaPack_Number |  | U16 |  |  |  |  | R | High 8 bits: number of battery packs in parallel Low 8 bits: number of strings in all packs
| 900E | Realtime_Capacity |  | U16 | 1 | % |  |  | R | Real-time remaining capacity
| 900F | Total_Voltage |  | U16 | 0.1 | V |  |  | R | total voltage
| 9010 | Total_Current |  | I16 | 0.1 | A |  |  | R | total current
| 9011 | Cell_Average_Temperature |  | I16 | 0.1 | ℃ |  |  | R | Average cell temperature
| 9012 | SOC |  | U16 | 1 | % |  |  | R | state of charge (physics)
| 9013 | SOH |  | U16 | 1 | % |  |  | R | healthiness
BMS protection, alarm messages | 9014 -- 9015 | BMS_Sys_Protect0 -- 1 |  | U16 |  |  |  |  | R | BMS system protection information 0-1
| 9016 -- 9017 | BMS_Sys_Alarm0 -- 1 |  | U16 |  |  |  |  | R | BMS system alarm messages 0-1
BMS version number | 9018 | Sofar_BMS_Version |  | ASCII |  |  |  |  | R | The lower 8 bits of the register hold the ASCII code, the default value of the official version is 'V'.
| 9019 | Sofar_BMS_Version |  | U16 |  |  |  |  | R | The lower 8 bits of the register are the software major version number 0-255
| 901A | Sofar_BMS_Version |  | U16 |  |  |  |  | R | The lower 8 bits of the register are the software non-standard version number 0-255
| 901B | Sofar_BMS_Version |  | U16 |  |  |  |  | R | The lower 8 bits of the register are the software minor version number 0-255
| 901C--901D | BMS_Sys_Protect2 -- 3 | [6 empty] | R | BMS system protection information 2-3
| 901E -- 901F | BMS_Sys_fault0 -- 1 | [6 empty] | R | BMS fault reservation
BMS Query Control Word | 9020 | BMS_Inquire |  | U16 |  |  |  |  | RW | Battery query control word Bit0-7: query battery Pack serial number, valid range 0~15, 0 means the 1st pack battery Bit8-11: query battery pack serial number, valid range 0~15, 0 means the 1st pack battery Bit12-15: Fault serial number of the query, valid range 0~5, 0 means the latest failure
BMS function switch | 9021 | BMS_Control |  | U16 |  |  |  |  | RW | Battery function switch control word Bit0-1: forced hibernation control: for 0, 1 reserved, for 2 hibernation; Bit2-3: current running log save control: 0-no save, 1-no action, 2-save; Bit4-7: reserved; Bit8-15: address of the battery to be controlled, FF for broadcast;
BMSOnline Status Table | 9022 | bms_group_online_bitmap |  | U16 |  |  | 0 | FFFF | R | Battery online status table Bit0 to bit15 indicate the minimum to maximum online status of the address respectively. Up to 16 battery online statuses are supported, with 1 indicating online and 0 indicating offline. For example: 0x03 for BTS battery, address 0x01 and 0x02 are online. 0x03 for GTX battery Addresses 0 and 1 are online.
BMSDormant Status Table | 9023 | bms_group_sleep_bitmap |  | U16 |  |  | 0 | FFFF | R | Battery hibernation status table, for the time being, only BTS batteries are supported, all other batteries are 0. Bit0 to bit15 indicate the hibernation status of the address from minimum to maximum respectively. 1 indicates hibernation. For example: 0x12 means the 0x02 address and 0x11 address of BTS battery are dormant.
BMSSerial Number | 9024 -- 902D | bms_sn0-9 |  | U16 |  |  |  |  | R | BMS device serial number
System forced charge/discharge command | 902E | bms_discharge_charge_mode |  | U16 |  |  |  |  | R | System forced charge/discharge instruction Description of bit0-bit7 values: 0: Normal 1：Forced recharge 2：Forced standby 3: Forced full charge bit8. 0=&gt;Prohibit charging 1=&gt;Allow charging bit9. 0=&gt;Prohibit discharge 1=&gt;Allow discharge
Maximum discharge current limit value | 902F | bms_Current_Discharge_Limit |  | I16 | 1 |  |  |  | R | BMS maximum discharge current limit value
Maximum charging current limit value | 9030 | bms_Current_Charge_Limit |  | I16 | 1 |  |  |  | R | BMS Maximum Charge Current Limit
| 9031 -- 903F | [8 empty] | reserve
| 9040 -- 9043 | AddressMask_BMS2_Realtime |  | U64 |  |  |  |  | R | Mask area for the 64 register address words starting at this address. Refer to the description of address 0x0040 |  | 0 | 0000000F
Battery Packs Real-time data | 9044 | Pack_RT_ID |  | U16 |  |  |  |  | R | Real-time data battery pack number. High 8 bits: Battery pack serial number Low 8 bits: battery pack pack serial number
| 9045 | Pack_RT_Timestamp |  | U32 |  |  |  |  | R | Real-time data timestamp Bit0-5: second, range 0-59 Bit6-11: minute, range 0-59 Bit12-16: hour, range 0-23 Bit17-21: day, range 1-31 Bit22-25: month, range 1-12 Bit26-31: year, range 0-63 (starting from 2000)
9046
| 9047 | Pack_RT_SN0 |  | U16 |  |  |  |  | R | Device RT Serial Number 0 (ASCII) Example: 0x5043 for "PC".
| 9048 -- 9050 | Pack_RT_SN1 -- 9 |  | U16 |  |  |  |  | R | Device serial number 1-9
| 9051 -- 9068 | Pack_RT_Cell_Voltage1 -- 24 |  | U16 | 0.001 | V |  |  | R | Cell RT 1-24 Voltage
| 9069 | Pack_RT_Cell_Max_Voltage |  | U16 | 0.001 | V |  |  | R | Maximum Cell Voltage
| 906A | Pack_RT_Cell_Min_Voltage |  | U16 | 0.001 | V |  |  | R | Minimum Cell Voltage
| 906B -- 906E | Pack_RT_Temperature1_Pack -- Pack_RT_Temperature4_Pack |  | I16 | 0.1 | ℃ |  |  | R | Battery pack RT temperature 1-4
| 906F | Pack_RT_Temperature_MOS |  | I16 | 0.1 | ℃ |  |  | R | MOS tube temperature
| 9070 | Pack_RT_Temperature_Env |  | I16 | 0.1 | ℃ |  |  | R | Ambient temperature inside the battery pack
| 9071 | Pack_RT_Current |  | I16 | 0.1 | A |  |  | R | Battery Pack Current
| 9072 | Pack_RT_Remaining_Capacity |  | U16 | 0.1 | Ah |  |  | R | remaining capacity
| 9073 | Pack_RT_FullCharge_Capacity |  | U16 | 0.1 | Ah |  |  | R | full capacity
| 9074 | Pack_RT_Cycles |  | U16 | 1 | times |  |  | R | Number of cycles
| 9075 | Pack_RT_Balance_State |  | U16 |  |  |  |  | R | Equalization status Bit0-15: Equalization status corresponding to section 1-16 cells 0: equalization off, 1: equalization on
| 9076 | Pack_RT_Alarm_State |  | U16 |  |  |  |  | R | warning status
| 9077 | Pack_RT_Protect_State |  | U16 |  |  |  |  | R | protected state
| 9078 | Pack_RT_Fault_State |  | U16 |  |  |  |  | R | fault state
| 9079 | Pack_RT_Total_Voltage |  | U16 | 0.1 | V |  |  | R | total voltage
| 907A | Pack_RT_SOC |  | U16 | 1 | % |  |  | R | SOC
| 907B | Pack_RT_Pack_Number |  | U16 |  |  |  |  | R | The total number of strings of the battery pack of this group of batteries
| 907C | Pack_RT_Cell_Number |  | U16 |  |  |  |  | R | Number of cell strings in a single battery pack of this group
| 907D -- 907F | [8 empty] | reserve
| 9080 -- 9083 | AddressMask_BMS3_Fault |  | U64 |  |  |  |  | R | Mask area for the 64 register address words starting at this address. Refer to the description of address 0x0040 |  | 0 | 0000000F
Battery Pack Failure Data | 9084 | Pack_Fault_ID |  | U16 |  |  |  |  | R | Real-time faulty battery Pack number. Bit0-7: query battery Pack serial number, valid range 0~15, 0 means the 1st pack battery Bit8-11: query battery pack serial number, valid range 0~15, 0 means the 1st pack battery Bit12-15: Fault serial number of the query, valid range 0~5, 0 means the latest failure
| 9085 -- 9086 | Pack_Fault_Timestamp |  | U32 |  |  |  |  | R | Fault data timestamp Bit0-5: second, range 0-59 Bit6-11: minute, range 0-59 Bit12-16: hour, range 0-23 Bit17-21: day, range 1-31 Bit22-25: month, range 1-12 Bit26-31: year, range 0-63 (starting from 2000)
| 9087 -- 9090 | Pack_Fault_SN0 -- 9 |  | U16 |  |  |  |  | R | Device Fault serial numbers 0-9
| 9091 -- 90A8 | Pack_Fault_Cell_Voltage1 -- 24 |  | U16 | 0.001 | V |  |  | R | Cell Fault 1-24 Voltage
| 90A9 | Pack_Fault_Cell_Max_Voltage |  | U16 | 0.001 | V |  |  | R | Maximum Cell Voltage
| 90AA | Pack_Fault_Cell_Min_Voltage |  | U16 | 0.001 | V |  |  | R | Minimum Cell Voltage
| 90AB -- 90AE | Pack_Fault_Temperature1_Pack -- Pack_Fault_Temperature4_Pack |  | I16 | 0.1 | ℃ |  |  | R | Battery pack Fault temperature 1-4
| 90AF | Pack_Fault_Temperature_MOS |  | I16 | 0.1 | ℃ |  |  | R | MOS tube temperature
| 90B0 | Pack_Fault_Temperature_Env |  | I16 | 0.1 | ℃ |  |  | R | Ambient temperature inside the battery pack
| 90B1 | Pack_Fault_Current |  | I16 | 0.1 | A |  |  | R | Battery Pack Current
| 90B2 | Pack_Fault_Remaining_Capacity |  | U16 | 0.1 | Ah |  |  | R | remaining capacity
| 90B3 | Pack_Fault_FullCharge_Capacity |  | U16 | 0.1 | Ah |  |  | R | full capacity
| 90B4 | Pack_Fault_Total_Voltage |  | U16 | 0.01 | V |  |  | R | total voltage
| 90B5 | Pack_Alarm_State |  | U16 |  |  |  |  | R | warning status
| 90B6 | Pack_Protect_State |  | U16 |  |  |  |  | R | protected state
| 90B7 | Pack_Fault_State |  | U16 |  |  |  |  | R | fault state
| 90B8 | Pack_Fault_Pack_Number |  | U16 |  |  |  |  | R | Total number of packs in this group
| 90B9 | Pack_Fault_Cell_Number |  | U16 |  |  |  |  | R | Number of cell strings in a single battery pack of this group
| 90BA | Pack_Cell_Info |  | U16 |  |  |  |  | RW | bit0-7:cell serial number, 0 means the first cell; bit8-15:enumeration type, indicating the data type of the electric core. (0-indicates the temperature of the battery cell, unit 0.1℃, I16) (1-indicates the voltage of the core, unit 0.001V, U16) (Other - reserved)
| 90BB | Pack_Cell_Data |  | U16/I16 |  |  |  |  | R | Data content, used in combination with 90BA
| 90BC-90BF | Pack_RT_Temperature5_Pack -- Pack_RT_Temperature8_Pack |  | I16 | 0.1 | ℃ |  |  | R | Battery pack RT temperature 5-8
| 90C0-90C3 | Pack_Fault_Temperature5_Pack -- Pack_Fault_Temperature8_Pack |  | I16 | 0.1 | ℃ |  |  | R | Battery pack Fault temperature 5-8
| 90C4-90FF | [8 empty] | reserve
| 9100-9103 | reserved |  | U64 | [5 empty] | reservations
battery pack | 9104 | balance bus voltage | U16 | U16 | 0.1 | V |  |  | R | Equalize bus voltage
| 9105 | balance current | I16 | I16 | 0.1 | A |  |  | R | Equalization current
| 9106-9109 | cell manufacture0-7 |  | ASCII*8 |  |  |  |  | R | Manufacturer of battery cells
| 910A | pack SOH |  |  | 0.1 | % |  |  | R | SOH
| 910B | pack capacity |  | U16 | 0.1 | Ah |  |  | R | PackRated Capacity
| 910C-911B | cell temperature1-16 |  | I16 | 0.1 | degC |  |  | R | Battery cell temperature
| 911C-911D | discharge Ah |  | U32 | 0.01 | Ah |  |  | R | Total life cycle dischargeAhnumber(0.01Ah)
| 911E-911F | chasrge Ah |  | U32 | 0.01 | Ah |  |  | R | Total life cycle chargingAhcount(0.01Ah)
| 9120-9121 | discharge Wh |  | U32 | 1 | Wh |  |  | R | Total Life Cycle DischargeWh(1Wh)
| 9122-9123 | chasrge Wh |  | U32 | 1 | Wh |  |  | R | Total Life Cycle ChargingWh(1Wh)
| 9124 | Pack_RT_Alarm_State |  | U16 |  |  |  |  | R | Alarm state 2
| 9125 | Pack_RT_Protect_State |  | U16 |  |  |  |  | R | Protection state 2
| 9126 | Pack_RT_Fault_State |  | U16 |  |  |  |  | R | Fault state 2
Note on H456: PF1VK175. -10000~-8000 corresponds to power factor -1~-0.8
Note on I456: PF1VK175. 8000~10000 corresponds to power factor 0.8~1

## Fault Bit Field Description
Table | Byte | Bit | bit field | serial number | note | alarm source | categorization | Design Categorization |  | Commercial and industrial projects | household storage project | LEO4
Fault1 | byte 0 | bit 0 | GridOVP | 001 | Grid overvoltage | DSP | externally | grids
|  | bit 1 | GridUVP | 002 | Grid undervoltage | DSP | externally
|  | bit 2 | GridOFP | 003 | Grid overfrequency | DSP | externally
|  | bit 3 | GridUFP | 004 | Grid underfrequency | DSP | externally
|  | bit 4 | GFCI | 005 | leakage current fault | DSP | externally
|  | bit 5 | OVRT | 006 | have an overhead error | DSP | externally
|  | bit 6 | LVRT | 007 | underwearing | DSP | externally
|  | bit 7 | IslandFault | 008 | island error (computing) | DSP | externally
| byte 1 | bit 0 | GridOVPInstant1 | 009 | Grid instantaneous value overvoltage1 | DSP
|  | bit 1 | GridOVPInstant2 | 010 | Grid instantaneous value overvoltage2 | DSP
|  | bit 2 | VGridLineFault | 011 | Grid line voltage error | DSP | externally
|  | bit 3 | InvVoltFault | 012 | Inverter voltage error | DSP
|  | bit 4 | RefluxFault | 013 | Anti-reverse current overload | DSP | externally
|  | bit 5 | VGridUnbalance | 014 | Grid voltage imbalance | DSP | externally
|  | bit 6 | InvOVPInstant | 015 | Inverter transient value overvoltage
|  | bit 7 | GridPhaseMutation | 016 | Grid Phase Change Sudden Change
Fault2 | byte 0 | bit 0 | HwADErrrIGrid | 017 | Grid current sampling error | DSP |  | sampling error
|  | bit 1 | HwADErrDCI(AC) | 018 | DCI Sampling Error (AC) | DSP
|  | bit 2 | HwADErrVGrid(DC) | 019 | Net pressure sampling error (DC) | DSP
|  | bit 3 | HwADErrVGrid (AC) | 020 | Net pressure sampling error (AC) | DSP
|  | bit 4 | HwGFCIFault(DC) | 021 | GFCI Sampling Error (DC) | DSP
|  | bit 5 | HwGFCIFault(AC) | 022 | GFCI Sampling Error (AC) | DSP
|  | bit 6 | HwADErrDCV | 023 | DCV sampling error | DSP
|  | bit 7 | HwADErrIdc | 024 | Input current sampling error | DSP
| byte 1 | bit 0 | HwADErrDCI(DC) | 025 | DCI Sampling Error (DC) | DSP
|  | bit 1 | HwADErrIdcBranch | 026 | Branch current sampling error | DSP
|  | bit 2 | PVLowImpedance | 027 | PV - Low impedance to ground
|  | bit 3 | PIDAbnormalOut | 028 | PID Exception Output
|  | bit 4 | ConsistentGFCI | 029 | Leakage current consistency error | DSP
|  | bit 5 | ConsistentVgrid | 030 | Net Pressure Consistency Error | DSP
|  | bit 6 | ConsistentDCI | 031 | DCI Conformance Error | DSP
|  | bit 7 | N-PE fault | 032 | neutral ground fault (NGF)
Fault3 | byte 0 | bit 0 | SpiCommFault(DC) | 033 | SPI communication error (DC) | DSP
|  | bit 1 | SpiCommFault(AC) | 034 | SPI communication error (AC) | DSP
|  | bit 2 | SChip_Fault | 035 | Chip Error (DC) | DSP
|  | bit 3 | MChip_Fault | 036 | Chip Error (AC) | DSP
|  | bit 4 | HwAuxPowerFault | 037 | Auxiliary power supply error | DSP
|  | bit 5 | InvSoftStartFail | 038 | Inverter soft start failure | DSP
|  | bit 6 | ArcShutdownAlarm | 039 | Arc shutdown protection | DSP | externally
|  | bit 7 | LowLightChkFail | 040 | Low light detection failure | DSP
| byte 1 | bit 0 | RelayFail | 041 | Relay detection failure | DSP |  | systems
|  | bit 1 | IsoFault | 042 | Low insulation impedance | DSP | externally
|  | bit 2 | PEConnectFault | 043 | grounding error | DSP | externally
|  | bit 3 | InputConfigError | 044 | Input mode setting error | DSP | externally
|  | bit 4 | CTDisconnect | 045 | CT error | DSP | externally
|  | bit 5 | ReversalConnect | 046 | Input reverse connection error | DSP | externally
|  | bit 6 | ParallelFault | 047 | parallelism error | DSP | externally
|  | bit 7 | SNTypeFault | 048 | Serial number error | DSP
Fault4 | byte 0 | bit 0 | TempErrBat | 049 | Battery temperature protection | DSP | externally | temp
|  | bit 1 | TempErrHeatSink1 | 050 | Radiator 1 temperature protection | DSP | externally
|  | bit 2 | TempErrHeatSink2 | 051 | Radiator 2 temperature protection | DSP | externally
|  | bit 3 | TempErrHeatSink3 | 052 | Radiator 3 temperature protection | DSP | externally
|  | bit 4 | TempErrHeatSink4 | 053 | Radiator 4 temperature protection | DSP | externally
|  | bit 5 | TempErrHeatSink5 | 054 | Radiator 5 temperature protection | DSP | externally
|  | bit 6 | TempErrHeatSink6 | 055 | Radiator 6 temperature protection | DSP | externally
|  | bit 7 | NTCFault | 056 | NTC failure
| byte 1 | bit 0 | TempErrEnv1 | 057 | Ambient temperature 1 protection | DSP | externally
|  | bit 1 | TempErrEnv2 | 058 | Ambient temperature 2 protection | DSP | externally
|  | bit 2 | TempErrInv1 | 059 | Module 1 Temperature Protection | DSP | externally
|  | bit 3 | TempErrInv2 | 060 | Module 2 Temperature Protection | DSP | externally
|  | bit 4 | TempErrInv3 | 061 | Module 3 Temperature Protection | DSP | externally
|  | bit 5 | TempDiffErrInv | 062 | Excessive module temperature difference | DSP
|  | bit 6 |  | 063
|  | bit 7 |  | 064
Fault5 | byte 0 | bit 0 | BusRmsUnbalance | 065 | Busbar RMS unbalance | DSP |  | over-undervoltage
|  | bit 1 | BusInstUnbalance | 066 | Busbar instantaneous value imbalance | DSP
|  | bit 2 | BusUVP | 067 | Bus undervoltage during grid connection | DSP
|  | bit 3 | BusZVP | 068 | Busbar Low Voltage | DSP
|  | bit 4 | PVOVP | 069 | PV overvoltage | DSP
|  | bit 5 | BatOVP | 070 | Battery overvoltage | DSP
|  | bit 6 | LLCBusOVP | 071 | LLCBus overvoltage protection | DSP
|  | bit 7 | SwBusRmsOVP | 072 | Bus Rms Software Overvoltage | DSP
| byte 1 | bit 0 | SwBusIOVP | 073 | Instantaneous software overvoltage on busbar | DSP
|  | bit 1 | FlyingCapOVP | 074 | Flying across capacitor overvoltage protection | DSP
|  | bit 2 | FlyingCapUVP | 075 | Flying across capacitor undervoltage protection | DSP
|  | bit 3 | PVUVP | 076 | PV undervoltage
|  | bit 4 |  | 077
|  | bit 5 |  | 078
|  | bit 6 |  | 079
|  | bit 7 |  | 080
Fault6 | byte 0 | bit 0 | SwBatOCP | 081 | Battery overcurrent software protection | DSP |  | amps
|  | bit 1 | DciOCP | 082 | Dci overcurrent protection | DSP
|  | bit 2 | SwIOCP | 083 | Output transient current protection | DSP
|  | bit 3 | SwBuckBoostOCP | 084 | BckBst Software Overcurrent | DSP
|  | bit 4 | SwAcRmsOCP | 085 | Inverter Rms current protection | DSP
|  | bit 5 | SwPvOCPInstant | 086 | PV transient software overcurrent | DSP
|  | bit 6 | IpvUnbalance | 087 | PV parallel uneven flow | DSP
|  | bit 7 | IacUnbalance | 088 | Output current imbalance | DSP
| byte 1 | bit 0 | SwPvOCP | 089 | PV software overcurrent protection | DSP
|  | bit 1 | IbalanceOCP | 090 | Balanced circuit overcurrent protection | DSP
|  | bit 2 | ResOver | 091 | resonant protection | DSP
|  | bit 3 | SwAcCBCFault | 092 | Software wave-by-wave current limit protection | DSP
|  | bit 4 | SwPvBranchOCP | 093 | PV branch software overcurrent (enabled by default)
|  | bit 5 | PriDCChgDischgOCP | 094 | Primary charge/discharge overcurrent protection
|  | bit 6 | SwBUSOCP | 095 | Software BUS overcurrent protection
|  | bit 7 |  | 096
Fault7 | byte 0 | bit 0 | HwLLCBusOVP | 097 | LLC bus hardware overvoltage | DSP |  | hardware signal
|  | bit 1 | HwBusOVP | 098 | Inverter bus hardware overvoltage | DSP
|  | bit 2 | HwBuckBoostOCP | 099 | BckBst Hardware Overcurrent | DSP
|  | bit 3 | HwBatOCP | 100 | Battery hardware overcurrent | DSP
|  | bit 4 | HwPriDCGaNFault | 101 | Primary side hardware GaN tube failure
|  | bit 5 | HwPVOCP | 102 | PV hardware overcurrent | DSP
|  | bit 6 | HwACOCP | 103 | AC Output Hardware Overcurrent | DSP
|  | bit 7 | HwDiffOCP | 104 | Hardware differential overcurrent
| byte 1 | bit 0 | MeterCommFault | 105 | Meter communication error | DSP | externally | Hardware signal reservation, overload
|  | bit 1 | SNMachineFault | 106 | Serial number model error | DSP
|  | bit 2 | HwVerError | 107 | Hardware version mismatch
|  | bit 3 | GeneratorStartupFail | 108 | Generator startup failure fault
|  | bit 4 | GeneratorOverload | 109 | Generator overload protection
|  | bit 5 | Overload1 | 110 | Overload protection 1 | DSP | externally
|  | bit 6 | Overload2 | 111 | Overload protection 2 | DSP | externally
|  | bit 7 | Overload3 | 112 | Overload protection 3 | DSP | externally
Fault8 | byte 0 | bit 0 | OverTempDerating | 113 | overheating and load shedding | DSP | External, Tips | unloading (of trucks) | This fault word is only used to generate an alarm and does not directly cause the system to enter a fault state.
|  | bit 1 | FreqDerating | 114 | frequency derating | DSP | External, Tips
|  | bit 2 | FreqLoading | 115 | Frequency loading | DSP | External, Tips
|  | bit 3 | VoltDerating | 116 | voltage drop | DSP | External, Tips
|  | bit 4 | VoltLoading | 117 | Voltage loading | DSP | External, Tips
|  | bit 5 | LowTempDerating | 118 | low-temperature load shedding | DSP
|  | bit 6 |  | 119
|  | bit 7 |  | 120
| byte 1 | bit 0 | SpdFail(DC) | 121 | Lightning protection fault (DC) | DSP | External, Tips | turn off (a machine or device)
|  | bit 1 | SpdFail(AC) | 122 | Lightning Fault Protection (AC) | DSP | External, Tips
|  | bit 2 | PermOutShortCircuitFail | 123 | Output short circuit fault
|  | bit 3 | BatLow | 124 | Low battery | DSP | External, Tips
|  | bit 4 | BatDchgProhibit | 125 | Battery Discharge Alarm | DSP | External, Tips
|  | bit 5 |  | 126
|  | bit 6 |  | 127
|  | bit 7 | BatReversalConnect | 128 | Battery input reverse connection protection
Fault9 | byte 0 | bit 0 | PermHwAcOCP | 129 | AC hardware overcurrent fault | DSP | externally | permanent nature
|  | bit 1 | PermBusOVP | 130 | Bus overvoltage fault | DSP | externally
|  | bit 2 | PermHwBusOVP | 131 | Bus Hardware Overvoltage Failure | DSP | externally
|  | bit 3 | PermIpvUnbalance | 132 | PV uneven flow failure | DSP | externally
|  | bit 4 | PermEPSBatOCP | 133 | EPS battery overcurrent fault | DSP | externally
|  | bit 5 | PermAcOCPInstant | 134 | Output transient overcurrent fault | DSP | externally
|  | bit 6 | PermIacUnbalance | 135 | AC current unbalance fault | DSP | externally
|  | bit 7 | PermInvStartFail | 136 | Inverter soft start failure fault
| byte 1 | bit 0 | PermInCfgError | 137 | Input mode setting malfunction | DSP | externally
|  | bit 1 | PermDCOCPInstant | 138 | input overcurrent fault | DSP | externally
|  | bit 2 | PermHwDCOCP | 139 | Input hardware overcurrent fault | DSP | externally
|  | bit 3 | PermRelayFail | 140 | Permanent relay failure | DSP | externally
|  | bit 4 | PermBusUnbalance | 141 | Bus unbalance fault | DSP | externally
|  | bit 5 | PermSpdFail(DC) | 142 | Lightning protection fault (DC) | DSP
|  | bit 6 | PermSpdFail(AC) | 143 | Lightning Fault Protection (AC) | DSP
|  | bit 7 | PermGridRlyFail | 144 | Grid relay failure
Fault10 | byte 0 | bit 0 | USBFault | 145 | USB malfunction | ARM |  | communication board
|  | bit 1 | WifiFault | 146 | WIFI failure | ARM
|  | bit 2 | BluetoothFault | 147 | Bluetooth failure | ARM
|  | bit 3 | RTCFault | 148 | RTC Clock Failure | ARM
|  | bit 4 | CommEEPROMFault | 149 | Communication board EEPROM error | ARM
|  | bit 5 | FlashFault | 150 | Communication board FLASH error | ARM
|  | bit 6 | BatPartOffline | 151 | Battery partially dropped
|  | bit 7 | SafetyVerFault | 152 | Safety version error | ARM | externally
| byte 1 | bit 0 | SCILose(DC) | 153 | SCI error (DC) | ARM
|  | bit 1 | SCILose (AC) | 154 | SCI error (AC) | ARM
|  | bit 2 | SCILose(Fuse) | 155 | SCI error (Fuse) | ARM
|  | bit 3 | SoftVerError | 156 | Inconsistent software versions | ARM | externally
|  | bit 4 | BMS1CommFault | 157 | Lithium battery 1 communication failure | ARM | externally
|  | bit 5 | BMS2CommFault | 158 | Lithium battery 2 communication failure | ARM | externally
|  | bit 6 | BMS3CommFault | 159 | Lithium battery 3 communication failure | ARM | externally
|  | bit 7 | BMS4CommFault | 160 | Lithium battery 4 communication failure | ARM | externally
Fault11 | byte 0 | bit 0 | ForceShutdown | 161 | force a computer to shut down | ARM | externally | Communication board shutdown, load shedding
|  | bit 1 | RemoteShutdown | 162 | Remote shutdown | ARM | externally
|  | bit 2 | Drms0Shutdown | 163 | Drms0 shutdown | ARM | externally
|  | bit 3 | PSCommFault | 164 | Power station communication failure shutdown
|  | bit 4 |  | 165 |  | ARM | externally
|  | bit 5 |  | 166 |  | ARM | externally
|  | bit 6 |  | 167 |  | ARM | externally
|  | bit 7 | AFCIForceShutdown | 168 | AFCI Forced Shutdown |  |  |  |  | √
| byte 1 | bit 0 | FanFault1 | 169 | Fan 1 failure | ARM | externally | peripheral component
|  | bit 1 | FanFault2 | 170 | Fan 2 failure | ARM | externally
|  | bit 2 | FanFault3 | 171 | Fan 3 failure | ARM | externally
|  | bit 3 | FanFault4 | 172 | Fan 4 failure | ARM | externally
|  | bit 4 | FanFault5 | 173 | Fan 5 Failure | ARM | externally
|  | bit 5 | FanFault6 | 174 | Fan 6 Failure | ARM | externally
|  | bit 6 | FanFault7 | 175 | Fan 7 Failure | ARM | externally
|  | bit 7 | HwBatHeatingFault | 176 | Heating Film Failure | ARM | externally
Fault12 | byte 0 | bit 0 | BMS OVP | 177 | BMS overvoltage protection | BMS | External, Tip | BMS
|  | bit 1 | BMS UVP | 178 | BMS undervoltage protection | BMS | External, Tip
|  | bit 2 | BMS OTP | 179 | BMS High Temperature Protection | BMS | External, Tip
|  | bit 3 | BMS UTP | 180 | BMS cryoprotection | BMS | External, Tip
|  | bit 4 | BMS OCP | 181 | BMS overcurrent protection | BMS | External, Tip
|  | bit 5 | BMS Short | 182 | BMS short circuit protection | BMS | External, Tip
|  | bit 6 | BMS VerFault | 183 | Inconsistent BMS versions | ARM | External, Tip
|  | bit 7 | BMS CAN VerFault | 184 | Inconsistent BMSCAN versions | ARM | External, Tip
| byte 1 | bit 0 | BMS CAN VerLow | 185 | BMS CAN version too low | ARM | External, Tip
|  | bit 1 | BatDischargeHTP | 186 | Battery discharge over-temperature protection
|  | bit 2 | BatDischargeLTP | 187 | Battery discharge low temperature protection
|  | bit 3 | BatChargeHTP | 188 | Battery charging over temperature protection
|  | bit 4 | AFCICommLose | 189 | Arc equipment communication failures | ARM | External, Tip
|  | bit 5 | BatChargeLTP | 190 | Battery charging low temperature protection | ARM
|  | bit 6 | PID_Output_Fail | 191 | PID repair failure | ARM
|  | bit 7 | PLC_Com_Fail | 192 | PLC module heartbeat loss
Fault13 | byte 0 | bit 0 | StrFuseALM1-1 | 193 | String fuse open 1-1 | FUSE |  | FUSE
|  | bit 1 | StrFuseALM1-2 | 194 | String fuse open 1-2 | FUSE
|  | bit 2 | StrFuseALM2-1 | 195 | String fuse open 2-1 | FUSE
|  | bit 3 | StrFuseALM2-2 | 196 | String fuse open 2-2 | FUSE
|  | bit 4 | StrFuseALM3-1 | 197 | String Fuse Open 3-1 | FUSE
|  | bit 5 | StrFuseALM3-2 | 198 | String fuse open 3-2 | FUSE
|  | bit 6 | StrFuseALM4-1 | 199 | String fuse open 4-1 | FUSE
|  | bit 7 | StrFuseALM4-2 | 200 | String fuse open 4-2 | FUSE
| byte 1 | bit 0 | StrFuseALM5-1 | 201 | String fuse open 5-1 | FUSE
|  | bit 1 | StrFuseALM5-2 | 202 | String fuse open 5-2 | FUSE
|  | bit 2 | StrFuseALM6-1 | 203 | String fuse open 6-1 | FUSE
|  | bit 3 | StrFuseALM6-2 | 204 | String fuse open 6-2 | FUSE
|  | bit 4 | StrFuseALM7-1 | 205 | String fuse open 7-1 | FUSE
|  | bit 5 | StrFuseALM7-2 | 206 | String fuse open 7-2 | FUSE
|  | bit 6 | StrFuseALM8-1 | 207 | String fuse open 8-1 | FUSE
|  | bit 7 | StrFuseALM8-2 | 208 | String fuse open 8-2 | FUSE
Fault14 | byte 0 | bit 0 | StrFuseALM9-1 | 209 | String fuse open 9-1 | FUSE
|  | bit 1 | StrFuseALM9-2 | 210 | String fuse open 9-2 | FUSE
|  | bit 2 | StrFuseALM10-1 | 211 | String fuse open 10-1 | FUSE
|  | bit 3 | StrFuseALM10-2 | 212 | String fuse open 10-2 | FUSE
|  | bit 4 | StrFuseALM11-1 | 213 | String fuse open 11-1 | FUSE
|  | bit 5 | StrFuseALM11-2 | 214 | String fuse open 11-2 | FUSE
|  | bit 6 | StrFuseALM12-1 | 215 | String fuse open 12-1 | FUSE
|  | bit 7 | StrFuseALM12-2 | 216 | String fuse open 12-2 | FUSE
| byte 1 | bit 0 | StrFuseALM13-1 | 217 | String fuse open 13-1 | FUSE
|  | bit 1 | StrFuseALM13-2 | 218 | String fuse open 13-2 | FUSE
|  | bit 2 | StrFuseALM14-1 | 219 | String fuse open 14-1 | FUSE
|  | bit 3 | StrFuseALM14-2 | 220 | String fuse open 14-2 | FUSE
|  | bit 4 | StrFuseALM15-1 | 221 | String fuse open 15-1 | FUSE
|  | bit 5 | StrFuseALM15-2 | 222 | String fuse open 15-2 | FUSE
|  | bit 6 | StrFuseALM16-1 | 223 | String Fuse Open 16-1 | FUSE
|  | bit 7 | StrFuseALM16-2 | 224 | String fuse open 16-2 | FUSE
Fault15 | byte 0 | bit 0 | InputFuseALM0 | 225 | Input safety open 0 | FUSE
|  | bit 1 | InputFuseALM1 | 226 | Input fuse open 1 | FUSE
|  | bit 2 | InputFuseALM2 | 227 | Input Fuse Open 2 | FUSE
|  | bit 3 | InputFuseALM3 | 228 | Input fuse open 3 | FUSE
|  | bit 4 | InputFuseALM4 | 229 | Input Fuse Open 4 | FUSE
|  | bit 5 | InputFuseALM5 | 230 | Input fuse open 5 | FUSE
|  | bit 6 | InputFuseALM6 | 231 | Input fuse open 6 | FUSE
|  | bit 7 | InputFuseALM7 | 232 | Input fuse open 7 | FUSE
| byte 1 | bit 0 | InputFuseALM8 | 233 | Input fuse open 8 | FUSE
|  | bit 1 | InputFuseALM9 | 234 | Input fuse open 9 | FUSE
|  | bit 2 | InputFuseALM10 | 235 | Input fuse open 10 | FUSE
|  | bit 3 | InputFuseALM11 | 236 | Input fuse open 11 | FUSE
|  | bit 4 | InputFuseALM12 | 237 | Input fuse open 12 | FUSE
|  | bit 5 | InputFuseALM13 | 238 | Input fuse open 13 | FUSE
|  | bit 6 | InputFuseALM14 | 239 | Input fuse open 14 | FUSE
|  | bit 7 | InputFuseALM15 | 240 | Input fuse open 15 | FUSE
Fault16 | byte 0 | bit 0 | CombinerOVGp1 | 241 |  |  |  | confluence
|  | bit 1 | CombinerOVGp2 | 242
|  | bit 2 | CombinerOVGp3 | 243
|  | bit 3 | CombinerOVGp4 | 244
|  | bit 4 | CombinerOVGp5 | 245
|  | bit 5 | CombinerOVGp6 | 246
|  | bit 6 | CombinerOVGp7 | 247
|  | bit 7 | CombinerOVGp8 | 248
| byte 1 | bit 0 | CombinerOVGp9 | 249
|  | bit 1 | CombinerOVGp10 | 250
|  | bit 2 | CombinerOVGp11 | 251
|  | bit 3 | CombinerOVGp12 | 252
|  | bit 4 | CombinerOVGp13 | 253
|  | bit 5 | CombinerOVGp14 | 254
|  | bit 6 | CombinerOVGp15 | 255
|  | bit 7 | CombinerOVGp16 | 256
Fault17 | byte 0 | bit 0 | CombinerUVGp1 | 257 |  |  |  | confluence
|  | bit 1 | CombinerUVGp2 | 258
|  | bit 2 | CombinerUVGp3 | 259
|  | bit 3 | CombinerUVGp4 | 260
|  | bit 4 | CombinerUVGp5 | 261
|  | bit 5 | CombinerUVGp6 | 262
|  | bit 6 | CombinerUVGp7 | 263
|  | bit 7 | CombinerUVGp8 | 264
| byte 1 | bit 0 | CombinerUVGp9 | 265
|  | bit 1 | CombinerUVGp10 | 266
|  | bit 2 | CombinerUVGp11 | 267
|  | bit 3 | CombinerUVGp12 | 268
|  | bit 4 | CombinerUVGp13 | 269
|  | bit 5 | CombinerUVGp14 | 270
|  | bit 6 | CombinerUVGp15 | 271
|  | bit 7 | CombinerUVGp16 | 272
Fault18 | byte 0 | bit 0 | CombinerOC1 | 273 |  |  |  | confluence
|  | bit 1 | CombinerOC2 | 274
|  | bit 2 | CombinerOC3 | 275
|  | bit 3 | CombinerOC4 | 276
|  | bit 4 | CombinerOC5 | 277
|  | bit 5 | CombinerOC6 | 278
|  | bit 6 | CombinerOC7 | 279
|  | bit 7 | CombinerOC8 | 280
| byte 1 | bit 0 | CombinerOC9 | 281
|  | bit 1 | CombinerOC10 | 282
|  | bit 2 | CombinerOC11 | 283
|  | bit 3 | CombinerOC12 | 284
|  | bit 4 | CombinerOC13 | 285
|  | bit 5 | CombinerOC14 | 286
|  | bit 6 | CombinerOC15 | 287
|  | bit 7 | CombinerOC16 | 288
Fault19 | byte 0 | bit 0 | CombinerOC17 | 289 |  |  |  | confluence
|  | bit 1 | CombinerOC18 | 290
|  | bit 2 | CombinerOC19 | 291
|  | bit 3 | CombinerOC20 | 292
|  | bit 4 | CombinerOC21 | 293
|  | bit 5 | CombinerOC22 | 294
|  | bit 6 | CombinerOC23 | 295
|  | bit 7 | CombinerOC24 | 296
| byte 1 | bit 0 | CombinerOC25 | 297
|  | bit 1 | CombinerOC26 | 298
|  | bit 2 | CombinerOC27 | 299
|  | bit 3 | CombinerOC28 | 300
|  | bit 4 | CombinerOC29 | 301
|  | bit 5 | CombinerOC30 | 302
|  | bit 6 | CombinerOC31 | 303
|  | bit 7 | CombinerOC32 | 304
Fault20 | byte 0 | bit 0 | CtrlBoardOTW | 305 | Control board over-temperature alarm |  |  | temp
|  | bit 1 | CtrlBoardOTP | 306 | Control board over-temperature protection
|  | bit 2 | CtrlBoardUTW | 307 | Control Board Low Temperature Alarm
|  | bit 3 | CtrlBoardNTCFail | 308 | Temperature sensor failure
|  | bit 4 |  | 309
|  | bit 5 |  | 310
|  | bit 6 |  | 311
|  | bit 7 |  | 312
| byte 1 | bit 0 | TempErrInv4 | 313 | Module 4 Temperature Protection
|  | bit 1 | TempErrInv5 | 314 | Module 5 Temperature Protection
|  | bit 2 | TempErrInv6 | 315 | Module 6 Temperature Protection
|  | bit 3 |  | 316
|  | bit 4 |  | 317
|  | bit 5 |  | 318
|  | bit 6 |  | 319
|  | bit 7 |  | 320
Fault21 | byte 0 | bit 0 | GridPhaseSeq | 321 | Grid phase sequence error |  |  | DSPM
|  | bit 1 | N2PEFault | 322 | phase-to-ground fault
|  | bit 2 | AntiSC | 323 | Short-circuit proof
|  | bit 3 | AntiSCDeviceFault | 324 | Short-circuit-proof equipment error
|  | bit 4 | DCRelayFault | 325 | DC Relay Error
|  | bit 5 | TempErrAntiSC | 326 | Temperature protection for short-circuit-proof modules
|  | bit 6 | TempErrIGBTLow | 327 | Module Temperature Low Protection
|  | bit 7 | AcStartTimeOut | 328 | AC Backstart Timeout
| byte 1 | bit 0 | OverModulation | 329 | overmodulation
|  | bit 1 | DeviceIDMarchErr | 330 | Device ID mismatch
|  | bit 2 | InCommFault | 331 | Internal communication alarms
|  | bit 3 | CarrierSynFault | 332 | carrier synchronization signal failure
|  | bit 4 | BusShortCircuit | 333 | Busbar short-circuit protection
|  | bit 5 |  | 334
|  | bit 6 |  | 335
|  | bit 7 |  | 336
Fault22 | byte 0 | bit 0 | CombinerRefluxFault1 | 337 |  |  |  | confluence
|  | bit 1 | CombinerRefluxFault2 | 338
|  | bit 2 | CombinerRefluxFault3 | 339
|  | bit 3 | CombinerRefluxFault4 | 340
|  | bit 4 | CombinerRefluxFault5 | 341
|  | bit 5 | CombinerRefluxFault6 | 342
|  | bit 6 | CombinerRefluxFault7 | 343
|  | bit 7 | CombinerRefluxFault8 | 344
| byte 1 | bit 0 | CombinerRefluxFault9 | 345
|  | bit 1 | CombinerRefluxFault10 | 346
|  | bit 2 | CombinerRefluxFault11 | 347
|  | bit 3 | CombinerRefluxFault12 | 348
|  | bit 4 | CombinerRefluxFault13 | 349
|  | bit 5 | CombinerRefluxFault14 | 350
|  | bit 6 | CombinerRefluxFault15 | 351
|  | bit 7 | CombinerRefluxFault16 | 352
Fault23 | byte 0 | bit 0 | CombinerRefluxFault17 | 353 |  |  |  | confluence
|  | bit 1 | CombinerRefluxFault18 | 354
|  | bit 2 | CombinerRefluxFault19 | 355
|  | bit 3 | CombinerRefluxFault20 | 356
|  | bit 4 | CombinerRefluxFault21 | 357
|  | bit 5 | CombinerRefluxFault22 | 358
|  | bit 6 | CombinerRefluxFault23 | 359
|  | bit 7 | CombinerRefluxFault24 | 360
| byte 1 | bit 0 | CombinerRefluxFault25 | 361
|  | bit 1 | CombinerRefluxFault26 | 362
|  | bit 2 | CombinerRefluxFault27 | 363
|  | bit 3 | CombinerRefluxFault28 | 364
|  | bit 4 | CombinerRefluxFault29 | 365
|  | bit 5 | CombinerRefluxFault30 | 366
|  | bit 6 | CombinerRefluxFault31 | 367
|  | bit 7 | CombinerRefluxFault32 | 368
Fault24 | byte 0 | bit 0 |  | 369 |  |  |  | temp
|  | bit 1 |  | 370
|  | bit 2 |  | 371
|  | bit 3 |  | 372
|  | bit 4 |  | 373
|  | bit 5 |  | 374
|  | bit 6 |  | 375
|  | bit 7 |  | 376
| byte 1 | bit 0 | HwInvMosFault | 377 | Inverter MSO tube failure |  |  | hardware signal
|  | bit 1 | HwEPSOCP | 378 | EPS output hardware overcurrent
|  | bit 2 | AFCICheckError | 379 | AFCI self-test error |  |  |  |  | √
|  | bit 3 | LoadShort | 380 | Load short circuit protection | [5 empty] | √
|  | bit 4 |  | 381
|  | bit 5 |  | 382
|  | bit 6 |  | 383
|  | bit 7 |  | 384
Fault25 | byte 0 | bit 0 | HwADFaultCail | 385 | Hardware sample bias error |  |  | peripheral component
|  | bit 1 | FanFault8 | 386 | Fan 8Failure
|  | bit 2 |  | 387
|  | bit 3 |  | 388
|  | bit 4 |  | 389
|  | bit 5 |  | 390
|  | bit 6 |  | 391
|  | bit 7 |  | 392
| byte 1 | bit 0 |  | 393 |  |  |  | ARM
|  | bit 1 |  | 394
|  | bit 2 |  | 395
|  | bit 3 |  | 396
|  | bit 4 |  | 397
|  | bit 5 |  | 398
|  | bit 6 |  | 399
|  | bit 7 |  | 400
Fault26 | byte 0 | bit 0 | AFCI0 | 401 | faulty pulling arc (physics) |  |  | arc pulling
|  | bit 1 | AFCI1 | 402 | faulty pulling arc (physics)
|  | bit 2 | AFCI2 | 403 | faulty pulling arc (physics)
|  | bit 3 | AFCI3 | 404 | faulty pulling arc (physics)
|  | bit 4 | AFCI4 | 405 | faulty pulling arc (physics)
|  | bit 5 | AFCI5 | 406 | faulty pulling arc (physics)
|  | bit 6 | AFCI6 | 407 | faulty pulling arc (physics)
|  | bit 7 | AFCI7 | 408 | faulty pulling arc (physics)
| byte 1 | bit 0 | AFCI8 | 409 | faulty pulling arc (physics)
|  | bit 1 | AFCI9 | 410 | faulty pulling arc (physics)
|  | bit 2 | AFCI10 | 411 | faulty pulling arc (physics)
|  | bit 3 | AFCI11 | 412 | faulty pulling arc (physics)
|  | bit 4 | AFCI12 | 413 | faulty pulling arc (physics)
|  | bit 5 | AFCI13 | 414 | faulty pulling arc (physics)
|  | bit 6 | AFCI14 | 415 | faulty pulling arc (physics)
|  | bit 7 | AFCI15 | 416 | faulty pulling arc (physics)
Fault27 | byte 0 | bit 0 | AFCI16 | 417 | faulty pulling arc (physics) |  |  | arc pulling
|  | bit 1 | AFCI17 | 418 | faulty pulling arc (physics)
|  | bit 2 | AFCI18 | 419 | faulty pulling arc (physics)
|  | bit 3 | AFCI19 | 420 | faulty pulling arc (physics)
|  | bit 4 | AFCI20 | 421 | faulty pulling arc (physics)
|  | bit 5 | AFCI21 | 422 | faulty pulling arc (physics)
|  | bit 6 | AFCI22 | 423 | faulty pulling arc (physics)
|  | bit 7 | AFCI23 | 424 | faulty pulling arc (physics)
| byte 1 | bit 0 | AFCI24 | 425 | faulty pulling arc (physics)
|  | bit 1 | AFCI25 | 426 | faulty pulling arc (physics)
|  | bit 2 | AFCI26 | 427 | faulty pulling arc (physics)
|  | bit 3 | AFCI27 | 428 | faulty pulling arc (physics)
|  | bit 4 | AFCI28 | 429 | faulty pulling arc (physics)
|  | bit 5 | AFCI29 | 430 | faulty pulling arc (physics)
|  | bit 6 | AFCI30 | 431 | faulty pulling arc (physics)
|  | bit 7 | AFCI31 | 432 | faulty pulling arc (physics)
Fault28 | byte 0 | bit 0 | AFCI1CommFault | 433 | AFCI1 communication failure | Protocol version error (ARM) |  | Protocol version error (ARM)
|  | bit 1 | AFCI2CommFault | 434 | AFCI2 communication failure
|  | bit 2 |  | 435
|  | bit 3 |  | 436
|  | bit 4 |  | 437
|  | bit 5 |  | 438
|  | bit 6 |  | 439
|  | bit 7 |  | 440
| byte 1 | bit 0 | ModifyOVP | 441 | Setting the overvoltage protection event
|  | bit 1 | ARMDSPProVerFault | 442 | Inconsistent ARM_DSP protocol versions
|  | bit 2 | ARMAFCIProVerFault | 443 | ARM_AFCI protocol version inconsistency
|  | bit 3 | ARMDCDCProVerFault | 444 | Inconsistent ARM_DCDC protocol versions
|  | bit 4 |  | 445
|  | bit 5 |  | 446
|  | bit 6 |  | 447
|  | bit 7 |  | 448
Fault29 | byte 0 | bit 0 | VGridNPEOver | 449 | Zero ground voltage too high | grids |  | grids
|  | bit 1 | SwPvBranchOCP | 450 | PV branch software overcurrent (not enabled by default)
|  | bit 2 | NLineDisconnect | 451 | N line open circuit fault
|  | bit 3 | RoCoFFault | 452 | Grid frequency change protection
|  | bit 4 | LostPhaseFault | 453 | phase failure
|  | bit 5 | SwPvCurBackUp | 454 | PV branch software backfill
|  | bit 6 | HwADFaultVInv | 455 | Inverter voltage sampling error
|  | bit 7 | HwADInvalidVInvEPS | 456 | Inverter EPS Sampling Failure Fault
| byte 1 | bit 0 | ConsistentFaultVbus | 457 | Bus voltage consistency error
|  | bit 1 | HwADErrIBus | 458 | Bus current sampling error
|  | bit 2 | ParallelOffgridSyncFault | 459 | Parallel off-grid startup synchronization failure |  |  |  | Off-grid startup synchronization not completed in parallel mode, entering fault state |  |  | √
|  | bit 3 | HwPriDCOCP | 460 | Primary hardware overcurrent protection
|  | bit 4 | OffgridDchgFault | 461 | Off-grid prohibition of discharge faults |  |  |  | Emergency power supply mode reaches off-grid disablement conditions then goes into fault and recovers after a period of time |  |  | √
|  | bit 5 |  | 462
|  | bit 6 |  | 463
|  | bit 7 | Disable | 464 | This bit disables
Fault30 | byte 0 | bit 0 | DCDCFault | 465 | DCDC failure | grids |  | aggregate
|  | bit 1 | BCUFault | 466 | BCU failure
|  | bit 2 | BMUFault | 467 | BMU failure
|  | bit 3 | PIDFault | 468 | PID failure
|  | bit 4 |  | 469
|  | bit 5 |  | 470
|  | bit 6 |  | 471
|  | bit 7 |  | 472
| byte 1 | bit 0 | DischgMosFault | 473 | Discharge MOS Failure
|  | bit 1 | ChgMosFault | 474 | Charging MOS Failure
|  | bit 2 | NTC Falut | 475 | Battery NTC failure
|  | bit 3 | Cell Fault | 476 | battery pack failure
|  | bit 4 | Cell Voltage Sample Fault | 477 | sampling fault
|  | bit 5 | Storage Exception | 478 | Storage anomaly
|  | bit 6 |  | 479
|  | bit 7 | Disable | 480 | This bit disables

## status message table
Table | Byte | Bit | bit field | serial number | note |  | Commercial and industrial projects | LEO4 | Models below50KW
State1 | byte 0 | bit 0 | GridUVDerating | 001 | Grid low-voltage load shedding(load shedding power for inverter models based on maximum output current * lowest grid phase voltage)
|  | bit 1 | OverTempDerating | 002 | overheating and load shedding
|  | bit 2 | BusOVDerating | 003 | Busbar overvoltage load shedding
|  | bit 3 | QLimitedP | 004 | reactive energy limited to active energy
|  | bit 4 | CmdPDerating | 005 | Command active load shedding(safety regulations)
|  | bit 5 | DRMsDerating | 006 | DRMs load shedding
|  | bit 6 | FeedInLimitation | 007 | Backflow prevention and load shedding
|  | bit 7 | RemotePCtrl | 008 | Remote active control(communication box)
| byte 1 | bit 0 | OVUVDerating | 009 | Gridovervoltage and undervoltagesafetyshedding (Grid overvoltage and undervoltage load shedding for safety regulations)
|  | bit 1 | OFDerating | 010 | overfrequency load shedding
|  | bit 2 | UFLoading | 011 | Underfrequency loading
|  | bit 3 | InnerDerating | 012 | Internal (other) load shedding (ratio/boost ratio load shedding)
|  | bit 4 | PVBranchOCDerating | 013 | PV branch circuit overcurrent load limit
|  | bit 5 | GridOVAlarming | 014 | Grid High Voltage Alarm
|  | bit 6 |  | 015
|  | bit 7 |  | 016
State2 | byte 0 | bit 0 | RemotePFCtrl | 017 | Remote PF control
|  | bit 1 | RemoteQCtrl | 018 | Remote reactive power(percentage of reactive power)control
|  | bit 2 | IndependenceQCtrl | 019 | Independent reactive power control
|  | bit 3 | NightRun | 020 | Nighttime operation status |  | √
|  | bit 4 |  | 021
|  | bit 5 |  | 022
|  | bit 6 |  | 023
|  | bit 7 |  | 024
| byte 1 | bit 0 | ForceOff | 025 | Forced shutdown (unique to 2nd generation, functional interface reserved for 3rd generation PV)
|  | bit 1 | RemoteOff | 026 | Remote shutdown (host computer)
|  | bit 2 | DRMs0Off | 027 | DRMs0 shutdown
|  | bit 3 | RefluxCommOff | 028 | Anti-reverse current communication protection shutdown |  | √
|  | bit 4 | EmergencyOff | 029 | emergency stop |  |  | √
|  | bit 5 |  | 030
|  | bit 6 |  | 031
|  | bit 7 |  | 032
State3 | byte 0 | bit 0 |  | 033
|  | bit 1 | OffgridDchgStop | 034 | off-limit status |  |  | √
|  | bit 2 | OngridChgDchgStop | 035 | Grid-connected charging and discharging ban |  |  | √
|  | bit 3 | EMS Off | 036 | EMS downtime |  |  | √
|  | bit 4 | AC Prechg Fail | 037 | Bus AC precharge abnormality |  |  | √
|  | bit 5 | EMS Error | 038 | BMS failure |  |  | √
|  | bit 6 |  | 039
|  | bit 7 |  | 040
| byte 1 | bit 0 |  | 041
|  | bit 1 |  | 042
|  | bit 2 |  | 043
|  | bit 3 |  | 044
|  | bit 4 |  | 045
|  | bit 5 |  | 046
|  | bit 6 |  | 047
|  | bit 7 |  | 048
State4 | byte 0 | bit 0 | BoostBreak1 | 049 | Boost tube damage state 1 | Boost |  |  | √
|  | bit 1 | BoostBreak2 | 050 | Boost tube damage state 2 |  |  |  | √
|  | bit 2 | BoostBreak3 | 051 | Boost tube damage state 3 |  |  |  | √
|  | bit 3 | BoostBreak4 | 052 | Boost tube damage state 4 |  |  |  | √
|  | bit 4 |  | 053
|  | bit 5 |  | 054
|  | bit 6 |  | 055
|  | bit 7 |  | 056
| byte 1 | bit 0 |  | 057
|  | bit 1 |  | 058
|  | bit 2 |  | 059
|  | bit 3 |  | 060
|  | bit 4 |  | 061
|  | bit 5 |  | 062
|  | bit 6 |  | 063
|  | bit 7 |  | 064
State5 | byte 0 | bit 0 |  | 065
|  | bit 1 |  | 066
|  | bit 2 |  | 067
|  | bit 3 |  | 068
|  | bit 4 |  | 069
|  | bit 5 |  | 070
|  | bit 6 |  | 071
|  | bit 7 |  | 072
| byte 1 | bit 0 |  | 073
|  | bit 1 |  | 074
|  | bit 2 |  | 075
|  | bit 3 |  | 076
|  | bit 4 |  | 077
|  | bit 5 |  | 078
|  | bit 6 |  | 079
|  | bit 7 |  | 080
State6 | byte 0 | bit 0 | RemoteDeratingEnable | 081 | Remote load shedding enable
|  | bit 1 | LogicIfDeratingEnable | 082 | Logical Interface Load-Down Enable
|  | bit 2 | FeedInLimitationEnable | 083 | Anti-backflow load shedding enable
|  | bit 3 |  | 084
|  | bit 4 |  | 085
|  | bit 5 |  | 086
|  | bit 6 |  | 087
|  | bit 7 |  | 088
| byte 1 | bit 0 |  | 089
|  | bit 1 |  | 090
|  | bit 2 |  | 091
|  | bit 3 |  | 092
|  | bit 4 |  | 093
|  | bit 5 |  | 094
|  | bit 6 |  | 095
|  | bit 7 |  | 096
State7 | byte 0 | bit 0 | IsoWarn | 097 | ISO Alerts
|  | bit 1 |  | 098
|  | bit 2 |  | 099
|  | bit 3 |  | 100
|  | bit 4 |  | 101
|  | bit 5 |  | 102
|  | bit 6 |  | 103
|  | bit 7 |  | 104
| byte 1 | bit 0 |  | 105
|  | bit 1 |  | 106
|  | bit 2 | FanWarn1 | 107 | Fan 1 alarm
|  | bit 3 |  | 108
|  | bit 4 |  | 109
|  | bit 5 |  | 110
|  | bit 6 |  | 111
|  | bit 7 |  | 112
State8 | byte 0 | bit 0 |  | 113
|  | bit 1 |  | 114
|  | bit 2 |  | 115
|  | bit 3 |  | 116
|  | bit 4 |  | 117
|  | bit 5 |  | 118
|  | bit 6 |  | 119
|  | bit 7 |  | 120
| byte 1 | bit 0 |  | 121
|  | bit 1 |  | 122
|  | bit 2 |  | 123
|  | bit 3 |  | 124
|  | bit 4 |  | 125
|  | bit 5 |  | 126
|  | bit 6 |  | 127
|  | bit 7 |  | 128
State9 | byte 0 | bit 0 |  | 129
|  | bit 1 |  | 130
|  | bit 2 |  | 131
|  | bit 3 |  | 132
|  | bit 4 |  | 133
|  | bit 5 |  | 134
|  | bit 6 |  | 135
|  | bit 7 |  | 136
| byte 1 | bit 0 |  | 137
|  | bit 1 |  | 138
|  | bit 2 |  | 139
|  | bit 3 |  | 140
|  | bit 4 |  | 141
|  | bit 5 |  | 142
|  | bit 6 |  | 143
|  | bit 7 |  | 144

## PCU Fault Bit Description
Warning1 (0x6024) | bit | ID | malfunctions | marginal notes
| 0 | 800
| 1 | 801 | IschgSoftStartFail | Charge soft start failure
| 2 | 802 | IsdchgSoftStartFail | Discharge soft start failure
| 3 | 803 | Fan1Fault | Fan 1 failure
| 4 | 804 | Fan2Fault | Fan 2 failure
| 5 | 805 | Fan3Fault | Fan 3 failure
| 6 | 806 | Fan4Fault | Fan 4 failure
| 7 | 807 | PCU VerFault | PCU version inconsistency
| 8 | 808 | HS1HighTempWarning | Radiator 1 over-temperature alarm
| 9 | 809 | EnvHighTempWarning | Ambient temperature over-temperature alarm
| 10 | 810 | HS2HighTempWarning | Radiator 2 over-temperature alarm
| 11 | 811
| 12 | 812
| 13 | 813 | StopChgWarning | Charge Prohibition Alarm
| 14 | 814 | StopDchgWarning | Discharge Prohibition Alarm
| 15 | 815 | BatUnbalancedWarning | Battery unbalance alarm
Warning2 (0x6025) | 0 | 816 | BusAvgOVWarning | Bus overvoltage alarm
| 1 | 817 | BusAvgUVWarning | Bus undervoltage alarm
| 2 | 818 | BatAvgOVWarning | Battery overvoltage alarm
| 3 | 819 | BatAvgUVWarning | Battery undervoltage alarm
| 4 | 820
| 5 | 821
| 6 | 822
| 7 | 823
| 8 | 824
| 9 | 825
| 11 | 827
| 12 | 828
| 13 | 829
| 14 | 830
| 15 | 831
Warning3 (0x6026) | 0 | 832
| 1 | 833
| 2 | 834
| 3 | 835
| 4 | 836
| 5 | 837
| 6 | 838
| 7 | 839
| 8 | 840
| 9 | 841
| 10 | 842
| 11 | 843
| 12 | 844
| 13 | 845
Warning4 (0x6027) | 0 | 848
| 1 | 849
| 2 | 850
| 3 | 851
| 4 | 852
| 5 | 853
| 6 | 854
| 7 | 855
| 8 | 856
| 9 | 857
| 10 | 858
| 11 | 859
| 12 | 860
| 13 | 861
| 14 | 862
| 15 | 863
Fault1 (0x6028) | 0 | 864 | HS1OverTempFault | Radiator 1 over-temperature protection
| 1 | 865 | OverTempFault_Env | Ambient temperature over-temperature protection
| 2 | 866 | SciCommFault | Sci communications failure
| 3 | 867 | Can1CommFault | Can1 communication failure
| 4 | 868 | Relay1Fail | Relay 1 failure
| 5 | 869 | HS2OverTempFault | Radiator 2 over-temperature protection
| 6 | 870 | Can2CommFault | Can2 communication failure
| 7 | 871 | Relay2Fail | Relay 2 failure
| 8 | 872 | SwBusInstantOVP | Busbar software overvoltage
| 9 | 873 | SwBusInstantUVP | Bus software undervoltage
| 10 | 874 | SwBatInstantOVP | Battery software overvoltage
| 11 | 875 | SwBatInstantUVP | Battery software undervoltage
| 12 | 876 | SwBatInstantOCP | Battery software overcurrent
| 13 | 877 | FlyingCap1OVP | Flying across capacitor 1 overvoltage
| 14 | 878 | FlyingCap2OVP | Flying across capacitor 2 overvoltage
| 15 | 879 | HwOCP | hardware overcurrent
Fault2 (0x6029) | 0 | 880 | unrecoverBusAvgOV | Permanent busbar overvoltage
| 1 | 881 | unrecoverBatAvgUV | Permanent battery undervoltage
| 2 | 882 | unrecoverOCPInstant | Permanent overcurrent
| 3 | 883 | unrecoverHwOCP | Permanent hardware overcurrent
| 4 | 884 | FlyingCap3OVP | Flying Span Capacitor 3 Overvoltage
| 5 | 885 | FlyingCap4OVP | Flying Span Capacitor 4 Overvoltage
| 6 | 886 | FlyingCap1UVP | Flying across capacitor 1 undervoltage
| 7 | 887 | FlyingCap2UVP | Flying across capacitor 2 undervoltage
| 8 | 888 | unrecoverRelay1Fail | Relay 1 permanent failure
| 9 | 889 | unrecoverRelay2Fail | Relay 2 permanent failure
| 10 | 890 | FlyingCap3UVP | Flying across capacitor 3 undervoltage
| 11 | 891 | FlyingCap4UVP | Flying across capacitor 4 undervoltage
| 12 | 892
| 13 | 893 | unrecoverBusSCP | Permanent short circuit protection
| 14 | 894 | unrecoverBatActFail | Permanent Battery Activation Failure
| 15 | 895 | unrecoverBusRPP | Permanent BUS reverse connection
Fault3 (0x602A) | 0 | 896 | BatteryStateErr | Battery status error
| 1 | 897 | PWMModeErr | PWM mode error
| 2 | 898 | BMSVerionErr | BMS version error
| 3 | 899 | BMSOVOCP | BMS overvoltage and overcurrent faults
| 4 | 900 | SwBatAvgOCP | Battery average overcurrent protection
| 5 | 901 | SwAvgOverloadP | Average value overload protection
| 6 | 902 | SwBusInstantOCP | Busbar software overcurrent
| 7 | 903 | SwCBCOCP | Software CBC overcurrent protection
| 8 | 904 | PackIDErr | PackID error
| 9 | 905 | StartupBusSCP | Start-up bus short-circuit protection
| 10 | 906 | BusAvgUVP | Busbar average undervoltage
| 11 | 907 | ChipClockFault | Chip Clock Failure
| 12 | 908 | PCSCanCommFault | Inverter CAN communication failure
| 13 | 909 | HeatsinkLowTempFault | Radiator Cold Temperature Failure
| 14 | 910 | EnyLowTempFault | Ambient low-temperature faults
| 15 | 911 | ADOffsetCalibrateFault | Sample Bias Calibration Fault
Fault4 (0x602B) | 0 | 912
| 1 | 913
| 2 | 914
| 3 | 915
| 4 | 916
| 5 | 917
| 6 | 918
| 7 | 919
| 8 | 920
| 9 | 921
| 10 | 922
| 11 | 923
| 12 | 924
| 13 | 925
| 14 | 926
| 15 | 927

## BDU Fault Message
Fault1 | bit | ID | malfunctions | marginal notes
| 0 | 928 | Reverse battery connection
| 1 | 929 | fusing fault
| 2 | 930
| 3 | 931
| 4 | 932
| 5 | 933
| 6 | 934
| 7 | 935
| 8 | 936
| 9 | 937
| 10 | 938
| 11 | 939
| 12 | 940
| 13 | 941
| 14 | 942
| 15 | 943

## DCDC Fault Bit Description
fault1 | bit | ID | malfunctions | marginal notes
| 0 | 600 | LowBusUVP | Low voltage side undervoltage
| 1 | 601 | SwLowBusOVP | Low Voltage Side Overvoltage Software
| 2 | 602 | HighBusUVP | High-side undervoltage
| 3 | 603 | SwHighBusOVP | High-side overpressure software
| 4 | 604 | FlyCapUnbalanceP | Fly across capacitor imbalance
| 5 | 605 | SwLowBusOCP | Low Voltage Side Overcurrent Software
| 6 | 606 | HwArmChipErr | ARM chip failure
| 7 | 607 | HwHVPolarityErr | High voltage reversal fault
| 8 | 608 | HwHighBusOVP | High-side overvoltage hardware
| 9 | 609 | HwLowBusOVP | Low Voltage Side Overvoltage Hardware
| 10 | 610 | HwLowBusOCP | Low Voltage Side Overcurrent Hardware
| 11 | 611 | HwIGBTDrvErr | IGBT driver failure
| 12 | 612 | HwVersionErr | Emergency version number error
| 13 | 613 | IsoFault | Insulation failure
| 14 | 614 | PEConnectFault | ground fault
| 15 | 615 | RelayFail | relay failure
fault2 | 0 | 616 | ArmCommFault | ARM Communication Failure
| 1 | 617 | PcsCommFault | PCS communication failure
| 2 | 618 | Pcu1CommFault | PCU1 communication failure
| 3 | 619 | Pcu2CommFault | PCU2 communication failure
| 4 | 620 | Pcu3CommFault | PCU3 communication failure
| 5 | 621 | Bms1CommFault | BMS1 communication failure
| 6 | 622 | Bms2CommFault | BMS2 communication failure
| 7 | 623 | Bms3CommFault | BMS3 communication failure
| 8 | 624 | DC1CommFault | DC1 communication failure
| 9 | 625 | DC2CommFault | DC2 communication failure
| 10 | 626 | DC3CommFault | DC3 communication failure
| 11 | 627 | DC4CommFault | DC4 communication failure
| 12 | 628 | DC5CommFault | DC5 communication failure
| 13 | 629 | DC6CommFault | DC6 communication failure
| 14 | 630 | ModuleOTP | Module over-temperature
| 15 | 631 | HwADZerodrift | drifting aimlessly
fault3 | 0 | 632 | HwHvFuseFault | High voltage fuse failure
| 1 | 633 | LvSideWakeUpFail | Low voltage side wake-up fault
| 2 | 634 | LvSideVakeUpTout | Low voltage side wakeup timeout
| 3 | 635 | EnvironmentOTP | Environmental over-temperature protection
| 4 | 636 | HwflyCapOVP | Flying across capacitor overvoltage hardware protection
| 5 | 637 | LowVolPolarityErr | Reverse connection fault on low voltage side
| 6 | 638 | HighVolRelayShort | High voltage side relay short circuit fault
| 7 | 639 | HighVolRelayOpenCircuit | High voltage side relay open circuit fault
| 8 | 640 | LowVolRelayShort | Low voltage side relay short circuit fault
| 9 | 641 | LowVolRelayOpenCircuit | Low voltage side relay open circuit fault
| 10 | 642
| 11 | 643 | HighVolLowVolDismatch | High and low voltage mismatch fault
| 12 | 644 | LowVolPrechargeFail | Precharge failure on low voltage side
| 13 | 645 | HighVolPrechargeFail | High voltage side precharge failure
| 14 | 646
| 15 | 647
fault4 | 0 | 648
| 1 | 649
| 2 | 650
| 3 | 651
| 4 | 652
| 5 | 653
| 6 | 654
| 7 | 655
| 8 | 656
| 9 | 657
| 10 | 658
| 11 | 659
| 12 | 660
| 13 | 661
| 14 | 662
| 15 | 663
Fault5 | 0 | 664
| 1 | 665
| 2 | 666
| 3 | 667
| 4 | 668
| 5 | 669
| 6 | 670
| 7 | 671
| 8 | 672
| 9 | 673
| 10 | 674
| 11 | 675
| 12 | 676
| 13 | 677
| 14 | 678
| 15 | 679
Fault6 | 0 | 680
| 1 | 681
| 2 | 682
| 3 | 683
| 4 | 684
| 5 | 685
| 6 | 686
| 7 | 687
| 8 | 688
| 9 | 689
| 10 | 690
| 11 | 691
| 12 | 692
| 13 | 693
| 14 | 694
| 15 | 695
Fault7 | 0 | 696
| 1 | 697
| 2 | 698
| 3 | 699
| 4 | 700
| 5 | 701
| 6 | 702
| 7 | 703
| 8 | 704
| 9 | 705
| 10 | 706
| 11 | 707
| 12 | 708
| 13 | 709
| 14 | 710
| 15 | 711
Fault8 | 0 | 712
| 1 | 713
| 2 | 714
| 3 | 715
| 4 | 716
| 5 | 717
| 6 | 718
| 7 | 719
| 8 | 720
| 9 | 721
| 10 | 722
| 11 | 723
| 12 | 724
| 13 | 725
| 14 | 726
| 15 | 727
Fault9 | 0 | 728 | VerDiffFault | Inconsistent software versions
| 1 | 729 | SCICommFault | SCI communication failure
| 2 | 730 | comm_can1_fault | CAN1 communication failure (DCDC intranet)
| 3 | 731 | comm_can2_fault | CAN2 communication failure (DCDC to battery)
| 4 | 732
| 5 | 733
| 6 | 734
| 7 | 735
| 8 | 736
| 9 | 737
| 10 | 738
| 11 | 739
| 12 | 740
| 13 | 741
| 14 | 742
| 15 | 743
Fault10 | 0 | 744 | DCDC CountWarn | DCDC quantity error
| 1 | 745 | PCU CountWarn | Incorrect number of PCUs
| 2 | 746 | BMS CountWarn | BMS quantity error
| 3 | 747 | fan1_warn | Fan 1 alarm (internal)
| 4 | 748 | fan2_warn | Fan 2 alarm (external)
| 5 | 749 | fan3_warn | Fan 3 alarm (external)
| 6 | 750 | MacConflict | MAC address conflict
| 7 | 751
| 8 | 752
| 9 | 753
| 10 | 754
| 11 | 755
| 12 | 756
| 13 | 757
| 14 | 758
| 15 | 759