## Cover
Shenzhen - SofarSolar
SofarSolar |  | Document code No: |  |  |  | version：V1.17
|  | Business Category Type |  | 业务类别： |  | Confidentiality Level: Confidential
SofarSolar - Modbus Communication protocol | [7 empty] | Page No.: Page 1 of 1
SofarSolar - Modbus Communication protocol
Distribution scope:Research and Development Department
版本号 Version | 修订人 Author of revision |  | 修订日期 Date of revision |  | 修改原因和内容 Change and Reason |  | 审核人 Reviewed by |  | 批准人 Approved by
V1.00 | 陈健聪(Eisen) |  | 2019-12-05 |  | Initial version；
V1.01 | 陈健聪(Eisen) |  | 2020-09-02 |  | Add register address and fault ID；
V1.02 | 陈健聪(Eisen) |  | 2020-12-02 |  | Register address and fault ID were added, and some register attribute errors were corrected；
V1.03 | 陈健聪(Eisen) |  | 2021-08-02 |  | Add PID configuration parameters and control parameters；
V1.04 | 刘永来(Left office) |  | 2021-08-11 |  | Increase the configuration parameters of PLC and BLE, increase the remote reset instruction; Extend the number of serial numbers used in production; Add peripheral corresponding table; Modified the PID configuration address; Added PLC heartbeat fault；
V1.05 | 陈健聪(Eisen) |  | 2021-08-31 |  | Fixed reactive power configuration type problem; Group string open alarm name change; Increase protocol version number；
V1.06 | 陈健聪(Eisen) |  | 2021-09-09 |  | Fixing the protocol version definition； Add chip code； Add lightning protecti on to recover the fault；
V1.07 | 陈健聪(Eisen) |  | 2021-11-03 |  | Modify the anti-flow mode definition, Add language definitions, Add offline mode, Add and upgrade the target chip, Increase resonant fault, Add serial number model error, Add ODM customization area, Increase the resonant sensitivity setting，
V1.08 | 陈健聪(Eisen) |  | 2022-03-02 |  | Update the PCU event list, Increase the internal protocol version number, Add the customer ID, AFCI version number address change, Add the status table, Increase the total power factor, Add battery protocol type, Add logical interface enable, Add PEN control, Increase the power grid overvoltage protection time high；
V1.09 | 陈健聪(Eisen) |  | 2022-04-24 |  | Increase ID15, 28, 93, 107, 136, 0404 address add PID status, Increase safety parameters, Add real-time SVG power control, Update the PCU event list, Add BDU to upgrade the target chip, Add 2 pieces of BDU data area；
V1.10 | 马国平(Martin) |  | 2022-05-30 |  | Increase total read-write power generation; Increase the total number of battery packets and the total number of battery packets of the reading group battery; Fault12-BMS protection description modification; The fault bit Fault11:165-167 is deleted；
V1.11 | 马国平(Martin) |  | 2022-06-27 |  | Added Fault28-Fault29 default does not enable bit area and zero ground voltage too high, PV branch software over-current fault; Added protocol version error (ARM); Add dry contact control mode Settings; New BOOT version number (primary DSP, secondary DSP); New PLC parameter area for power carrier communication; New battery parameters - communication protocol 11: dynamic;
V1.12 | 马国平(Martin) |  | 2022-07-27 |  | New MODBUS protocol, new PCU voltage and current calibration coefficient; New register 0x11C4~0x11C8: power station communication interrupt protection function register; Added ID164 Fault11-byte0-bit3 "PSCommFault" "Power station communication fault shutdown "; New register 0x200D: protocol setup register; The total power generation is modified to write only. Address 0x1046 Add battery parameters - Communication protocol 11:BTS 5K and modify battery parameters - Communication protocol 12: Action PCU fault bit Fault3, added PCU fault bit bit6:SwBusInstantOCP: bus software overflow; bit8:PackIDErr: PackID error；
V1.13 | 马国平(Martin) |  | 2022-08-31 |  | Enable reserved address, add protocol version number reading (ARM/DSPM/DSPL); New Fault2.byte1.bit7 neutral ground fault; New Fault9.byte1.bit grid relay fault; New battery information area to add "real-time battery number"; Added "inverter rated power", the unit is 0.1kW, read only; Added "total number of group strings/total number of battery", read-only; Add the number of the specified channel of the operation and the corresponding string/battery rating; New 0x0005: solarmax protocol; Added CT variable ratio setting; New hard anti-countercurrent switch; Modify the description of the Italian test S/F; Modify the description of the fault bit field and delete the repetition of the meter communication fault; Modify PLC parameter area of power carrier communication;
V1.14 | 马国平(Martin) |  | 2022-10-25 |  | Added fault bit HwDiffOCP/ hardware differential overcurrent; PCU SN code type ASCII changed to U16; DSPStatus1-8 Internal debug information (in the internal information area) duplication definition removed; The internal information is the debugging information content of the LCD display, and the prompt description is added; Add file type upgrade and progress display; Added the first flight BMS software version read; Languages added 14. Czech; Add setting overvoltage protection event; New DCDC data area (0x5000-0x5FFF) and fault bit description; New DCDC-ARM/DSP upgrade flag; Two fault flag bits were added to PCU; Dry contact control changed from 0x1147(not used) to 0x1064, reserved for wet contact control;
V1.15 | 马国平(Martin) |  | 2022-12-26 |  | The file type is changed from BIT to BYTE. Add safety file package Settings; ID93:PV branch software overflow (enabled by default); AFCI upgrade, AFCI chip code using the new standard, the chip type changed to 0x42; New collector mode; Add remote shutdown load shedding enable bit; Increase the average undervoltage bit of ID906 bus; Increasing the number of valid scanning points of IV curve; VersionType was added to enable the currently active protocol version. Added PVUVP(PV undervoltage); The measured packet page is added to supplement and remark the address description, which is continuously updated.
V1.16 | 马国平(Martin) |  | 2023-02-27 |  | Added ID15/16: invert instantaneous value overvoltage/power grid phase change mutation,ID118: low temperature load drop,ID186-188/190: battery discharge/charge, over temperature/low temperature protection,0x069C-06B3: Increase the power statistics of the current month,0x9020/908 4 Modify description: The range of control words is all starting from 1,0xA07D: Modify Description: Korean DEV-AVM protocol test flag. Adjustment and compression simplify the format and content of registers. This document is for internal use, and the corresponding score (point) table of each sub-model should be provided for external use. Maintenance requires the first total table, after the sub-table (point) are synchronized maintenance.
V1.17 | 马国平(Martin) |  | 2023-04-27 |  | The range of control words starts at 0. That is, 0 represents the first packet of data, also represents the first group of batteries; EP added a timing upgrade function; Add PCU fault bit ID907/908; Increase 027PV- low ground impedance; Increase the passing flow protection of PV branch; Added remote upgrade support package;

## Agreement Description
Write Format
Device Address | Function Code | Start Address |  | Write Register No. |  | Write Byte No. | Data to write in |  |  |  |  | CRC
1 Byte | 1 Byte | Hi Byte | Low Byte | Hi Byte | Low Byte | 1 Byte | Hi Byte 1 | Low Byte 1 | … | Hi Byte N | Low Byte N | Low Byte | Hi Byte
Broadcast Address:0x00; Device Address:1-247 | Write Function Code:0x10 | [5 empty] | For 32bits or 64bit data, it will be sent by Big-endian mode if there is no special explanation. For example, sequence to send a 32bits data: byte3, byte2, byte1, byte0 |  |  |  |  | Modbus-CRC16
Response Format of Write
Device Address | Function Code | Start Address |  | Write Register No. |  | CRC
1 Byte | 1 Byte | Hi Byte | Low Byte | Hi Byte | Low Byte | Low Byte | Hi Byte
Slave Address | Write Function Code:0x10 |  |  |  |  | Modbus-CRC16
Read Format
Device Address | Function Code | Start Address |  | Read Register No. |  | CRC
1 Byte | 1 Byte | Hi Byte | Low Byte | Hi Byte | Low Byte | Low Byte | Hi Byte
Device Address:1-247 | ReadFunction Code:0x03 |  |  |  |  | Modbus-CRC16
Response Format of Read
Device Address | Function Code | Data Byte No. | Response register data |  |  |  |  | CRC
1 Byte | 1 Byte | 1 Byte | Hi Byte 1 | Low Byte 1 | … | Hi Byte N | Low Byte N | Low Byte | Hi Byte
Slave Address | ReadFunction Code:0x03 |  | For 32bits or 64bit data, it will be sent by Big-endian mode if there is no special explaination. For example , sequence to send a 32bits data: byte3,byte2,byte1,byte0 |  |  |  |  | Modbus-CRC16
Abnormal Response
Device Address | Function Code | Error Code |  | CRC
1 Byte | 1 Byte | 1 Byte |  | Low Byte | Hi Byte
Slave Address | Abnormal Function Code:0x90 | See Error Code List |  | Modbus-CRC16
Error code
value | Notes
1 | Illegal function
2 | Invalid data address
3 | Invalid data value
4 | Slave equipment failure
7 | Busy with slave equipment
Read and write explanation
Value | Name | Explanation
R | Readable | Readable registers
W | Writable | Writable registers
V | Volatile | Variable registers, support frequent write operations

## Address Description
功能名 | Function name | register address | fields | type | accuracy | units | min | max | Properties | 说明 | Description | Confidential | Mask computation |  | Support single register read | Support single register write | Register linking is supported | Register concatenation is supported | 备注(Remarks) | Remarks
一、General（0x0040-0x007F） | 一、General（0x0040-0x007F）
掩码区 本64个连续地址 | " Masked Area This 64 contiguous address " | 0040 | AddressMask_General1 | U64 |  |  |  |  | R | 本地址开始的64个寄存器地址字的掩码区。 本字段每一位对应本字段64个地址的有效性（每一位对应一个寄存器地址，包括本字段地址）。 对应位为0代表无效，为1代表有效。 例：0x0000 0x0000 0x0000 0x001F表示0x0044地址功能有效，后面的掩码区的含义一致，并对地址区间做合并处理，不单列。 | Mask area for the 64 register address words starting at this address. Each bit of this field corresponds to the validity of the 64 addresses in this field (each bit corresponds to a register address, including the address of this field). A corresponding bit of 0 means invalid, a 1 means valid. Example: 0x0000 0x0000 0x0000 0x001F means that the 0x0044 address function is valid, followed by the same meaning of the mask area and a merged treatment of the address interval, not listed separately. | End-users | 00000000 | 0000000F |  |  | Start address length | Start address length | 从地址0x0040到地址0x004F的16个地址有效性 | 16 address validities from address 0x0040 to address 0x004F
|  | 0041 | [9 empty] | End-users | [6 empty] | 从地址0x0050到地址0x005F的16个地址有效性 | 16 address validities from address 0x0050 to address 0x005F
|  | 0042 | [9 empty] | End-users | [6 empty] | 从地址0x0060到地址0x006F的16个地址有效性 | 16 address validities from address 0x0060 to address 0x006F
|  | 0043 | [9 empty] | End-users | [6 empty] | 从地址0x0070到地址0x007F的16个地址有效性 | 16 address validities from address 0x0070 to address 0x007F
本协议版本号 | Version number of this agreement | 0044 | Modbus_Protocol_Version | BCD16 |  |  | 1.07 | 99.99 | R | 本协议版本号。 协议版本号与本协议封皮中的版本号相对应。 | Version number of this protocol. The protocol version number corresponds to the version number in the jacket of this protocol. | End-users | [6 empty] | 注：Modbus协议版本号（BCD码） 0-7位表示小版本号，其中0-3位表示低位版本数字，4-7位表示高位版本数字。 8-15位表示大版本号，其中8-11位表示低位版本数字，12-15位表示高位版本数字。 例：值0x1234表示协议版本号为12.34 | Note: Modbus protocol version number (BCD code) Bits 0-7 indicate the minor version number, where bits 0-3 indicate the low version number and bits 4-7 indicate the high version number. Bits 8-15 indicate a major version number, where bits 8-11 indicate a low version number and bits 12-15 indicate a high version number. Example: the value 0x1234 indicates a protocol version number of 12.34
芯片代号 (不对外开放) | Chip Code (not available to the public) | 0045 | COMM_MCU_Code | ASCII |  |  |  |  | R | 通讯芯片代号。 | Communication chip designator. | End-users | [6 empty] | 参考芯片编码规范，不对外开放。 需将ASCII码转换成对应字符 例：地址0x0045读取为0x4730表示“G0” | Reference chip coding specification, not available to the public. ASCII code needs to be converted to the corresponding character Example: address 0x0045 read as 0x4730 means G0""
|  | 0046 | CTRL1_MCU_Code | ASCII |  |  |  |  | R | 1号控制芯片代号。 | Control chip code number 1. | End-users
|  | 0047 | CTRL2_MCU_Code | ASCII |  |  |  |  | R | 2号控制芯片代号。 | Control chip code number 2. | End-users
|  | 0048 -- 0051 | MCU_Code_Rsvd1 -- 10 | [6 empty] | MCU编码预留地址1-10（10个） | MCU code reserved addresses 1-10 (of 10)
内部通信协议 版本号 | Internal communication protocol-Version number | 0052 | Protocol_ARM-DSPM |  |  |  | 0 | 0xFFFF | R | ARM和DSPM之间的协议版本号。 高8位对应ARM-DSPM的协议版本号， 低8位对应DSPM-ARM的协议版本号。 | Version number of the protocol between ARM and DSPM. The high 8 bits correspond to the ARM-DSPM protocol version number. The lower 8 bits correspond to the DSPM-ARM protocol version number. | End-users | [6 empty] | 协议版本号需要一致才能正常使用逆变器 根据机型查看是否使用了此功能 例1：0x0102表示ARM-DSPM的协议版本号为001，DSPM-ARM的协议版本号为002 例2：0x0203表示ARM-DSPS的协议版本号为002，DSPS-ARM的协议版本号为003 例3：0x0304表示DSPM-DSPS的协议版本号为003，DSPS-DSPM的协议版本号为004 | The protocol version number needs to be the same for the inverter to work properly Check if this function is used according to the model Example 1: 0x0102 means the protocol version number of ARM-DSPM is 001, the protocol version number of DSPM-ARM is 002 Example 2: 0x0203 means the protocol version number of ARM-DSPS is 002, the protocol version number of DSPS-ARM is 003 Example 3: 0x0304 means the protocol version number of DSPM-DSPS is 003 and the protocol version number of DSPS-DSPM is 004
|  | 0053 | Protocol_ARM-DSPS |  |  |  | 0 | 0xFFFF | R | ARM和DSPS之间的协议版本号。 高8位对应ARM-DSPS的协议版本号， 低8位对应DSPS-ARM的协议版本号。 | Protocol version number between ARM and DSPS. The high 8 bits correspond to the ARM-DSPS protocol version number, the The lower 8 bits correspond to the DSPS-ARM protocol version number. | End-users
|  | 0054 | Protocol_DSPM-DSPS |  |  |  | 0 | 0xFFFF | R | DSPM和DSPS之间的协议版本号。 高8位对应DSPM-DSPS的协议版本号， 低8位对应DSPS-DSPM的协议版本号。 | Protocol version number between DSPM and DSPS. The high 8 bits correspond to the DSPM-DSPS protocol version number, the The lower 8 bits correspond to the DSPS-DSPM protocol version number. | End-users
|  | 0055 -- 0065 | Protocol_Version_Rsvd4 -- 20 | [6 empty] | 协议版本预留地址4-20（17个） | Protocol version reservation addresses 4-20 (17)
|  | 0066 -- 007D | [7 empty] | 预留 | Reserved
客户ID | Customer ID | 007E -- 0007F | 客户ID_0 -- 1 | [5 empty] | RW | 区分不同客户使用的ID0-1。 参考客户编码规范 客户ID_0：用于标记客户ID，如默认首航为0x0000。 客户ID_1：备用拓展 | Distinguishes IDs 0-1 used by different customers. Refer to customer coding specification Customer ID_0: used to mark the customer ID, e.g. default first flight is 0x0000. Customer ID_1: alternate expansion | End-users | [6 empty] | 例：天合0x0001、创维0x0002等。 | Example: Trina 0x0001, Skyworth 0x0002, etc.
二、Real-time data area(0x0400-0x07FF)
2.1System Information(0x0400-0x047F)
|  | 0400 -- 0403 | AddressMask_Realtime_SysInfo1 | U64 |  |  |  |  | R | 本地址开始的64个寄存器地址字的掩码区。 参看地址0x0040的说明 | Mask area for the 64 register address words starting at this address. Refer to the description of address 0x0040 | End-users | 00000000 | 0000000F
运行状态 | Operational status | 0404 | SysState | U16 |  |  |  |  | R | 运行状态。 0：等待状态 1：检测状态 2：并网状态 3：应急供电状态 4：可恢复故障状态 5：永久性故障状态 6：升级状态 7：自充电状态 8：SVG状态 9：PID状态 | Operational status. 0: Waiting status 1: Detection status 2: Grid-connected status 3: Emergency power state 4: Recoverable fault state 5: Permanent fault state 6: Upgrade status 7: Self-charging state 8: SVG state 9: PID state | End-users | [6 empty] | 逆变器的运行状态，3、6-9的状态区分机型 例：0x0004表示逆变器处于可恢复故障状态 | Operating status of the inverter, the status of 3, 6-9 distinguishes between models Example: 0x0004 means that the inverter is in a recoverable fault state
故障信息表 2-1 | Fault Information Sheet 2-1 | 0405 -- 0416 | Fault1 -- 18 | U16 |  |  |  |  | R | 故障信息表1-18（18个）。 记录逆变器的故障信息，还有扩展的19-30地址在0x0432-043D | Fault information tables 1-18 (18). Records fault messages for the inverter, and also the extended 19-30 addresses at 0x0432-043D | End-users | [6 empty] | 对应故障信息查看此表格的另外一张工作表“故障位域说明” 例：从0x0405读取值为0x0002表示逆变器有电网欠压的故障 | Example: a value of 0x0002 from 0x0405 means that the inverter has a grid undervoltage fault"
并网等待时间 | Grid connection waiting time | 0417 | Countdown | U16 | 1 | 秒 |  |  | R | 并网等待时间(开机倒计时) | Grid connection waiting time (countdown to switch-on) | End-users | [6 empty] | 并网等待时间，可供查看的开机倒计时 例：0x003C指开机时间为60秒 | Grid connection waiting time, viewable countdown to switch on Example: 0x003C refers to a start-up time of 60 seconds
温度 | Temperature | 0418 -- 0419 | Temperature_Env1 -- 2 | I16 | 1 | ℃ |  |  | R | 环境温度1-2（2个） | Ambient temperature 1-2 (2) | End-users | [6 empty] | 例：0x0001指环境温度1为1℃ | Example: 0x0001 means that the ambient temperature1 is 1°C
|  | 041A -- 041F | Temperature_HeatSink1 -- 6 | I16 | 1 | ℃ |  |  | R | 散热器温度1-6（6个） | Heat sink temperature 1-6 (6) | End-users | [6 empty] | 是否具备此功能与机型相关，可根据掩码查看是否使用对应寄存器 案例请查看0x0418地址说明 | Availability of this function is related to the model, you can check whether the corresponding register is used according to the mask For example, please check the 0x0418 address description
|  | 0420 -- 0422 | Temperature_Inv1 -- 3 | I16 | 1 | ℃ |  |  | R | 模块温度1-3（3个） | Module temperature 1-3 (3) | End-users
|  | 0423 -- 0425 | Temp_Rsvd1 -- 3 | I16 | 1 | ℃ |  |  | R | 预留温度1-3（3个） | Reserved temperature 1-3 (3) | End-users
发电、运行时间 | Power generation, running time | 0426 | GenerationTime_Today | U16 | 1 | 分钟 |  |  | R | 当日发电时间 | Power generation time for the day | End-users | [6 empty] | 逆变器今日的发电时间，并网后开始计时 例：0x0001指当日发电1分钟 | Inverter's generation time for the day, starts after grid connection Example: 0x0001 refers to 1 minute of power generation for the day
|  | 0427 -- 0428 | GenerationTime_Total | U32 | 1 | 分钟 |  |  | R | 总发电时间 | Total power generation time | End-users | [6 empty] | 逆变器并网后开始计时，占用两个寄存器，例：0x0000 0x087E指总发电时间为2174分钟 | Inverter starts timing after grid connection, occupies two registers, example: 0x0000 0x087E means total power generation time of 2174 minutes
|  | 0429 -- 042A | ServiceTime_Total | U32 | 1 | 分钟 |  |  | R | 总运行时间 | Total runtime | End-users | [6 empty] | 逆变器上电开始计时，占用两个寄存器，例：0x0000 0x09C5指总运行时间为2501分钟 | The inverter starts timing when it is connected to the grid, occupies two registers, e.g. 0x0000 0x09C5 means the total running time is 2501 minutes
绝缘阻抗 | Insulation impedance | 042B | InsulationResistance | U16 | 1 | kΩ |  |  | R | 绝缘阻抗 | Insulation Impedance | End-users | [6 empty] | 绝缘阻抗大小，逆变器在检测状态检测 | Insulation impedance size, the inverter detects in the detection state
系统时间 2-1 | System time 2-1 | 042C | SysTime_Year | U16 |  |  |  |  | R | 系统时间-年 | System Time - Year | End-users | [6 empty] | 实际年份用2000年加上读出来的数据 例：0x0016指2022年 | Actual year in 2000 plus the read out data Example: 0x0016 refers to the year 2022
|  | 042D | SysTime_Month | U16 |  |  |  |  | R | 系统时间-月 | System Time - Months | End-users | [6 empty] | 例：0x0005指5月 | Example: 0x0005 refers to the month of May
|  | 042E | SysTime_Date | U16 |  |  |  |  | R | 系统时间-日 | System time - day | End-users | [6 empty] | 例：0x000F指15日 | Example: 0x000F refers to the 15th
|  | 042F | SysTime_Hour | U16 |  |  |  |  | R | 系统时间-时 | System Time - Hour | End-users | [6 empty] | 例：0x0010指16时 | Example: 0x0010 refers to the 16th hour
|  | 0430 | SysTime_Minute | U16 |  |  |  |  | R | 系统时间-分 | System Time - Minute | End-users | [6 empty] | 例：0x0020指32分 | Example: 0x0020 refers to 32 minutes
|  | 0431 | SysTime_Second | U16 |  |  |  |  | R | 系统时间-秒 | System time-second | End-users | [6 empty] | 例：0x0030指48秒 | Example: 0x0030 refers to 48 seconds
故障信息表 2-2 | Fault Information Sheet 2-2 | 0432 -- 043D | Fault19 -- 30 | U16 |  |  |  |  | R | 故障信息表19-30（12个）。 记录逆变器的故障信息，前18个在0x0418地址 | Fault message table 19-30 (12). Record fault messages for the inverter, first 18 at address 0x0418 | End-users | [6 empty] | 对应故障信息查看此表格的另外一张工作表“故障位域说明”，案例请查看0x0405地址备注 | For the corresponding fault information see the other worksheet of this form "Fault Bit Field Description", for the case see 0x0405 Address Remarks
|  | 043E -- 043F | [7 empty] | 预留 | Reserved
|  | 0440 -- 0443 | AddressMask_Realtime_SysInfo2 | U64 |  |  |  |  | R | 本地址开始的64个寄存器地址字的掩码区。 参看地址0x0040的说明 | Mask area for the 64 register address words starting at this address. Refer to the description of address 0x0040 | End-users | 00000000 | 0000000F
|  | 0444 | Production_Code | U16 | [5 empty] | 预留 | Reserved
机器序列号 2-1 | Machine serial number 2-1 | 0445 -- 044C | Serial_Number0 -- 7 | ASCII |  |  |  |  | R | 机器序列号Serial_Number0-7（8个，表示序列号第1-16位），第17-20位在寄存器地址0x0470和0x0471 | Machine serial number Serial_Number0-7 (8, indicating serial number bits 1-16), bits 17-20 at register addresses 0x0470 and 0x0471 | End-users | [6 empty] | 解析需要查看DCC的条码规则定义文档 Serial_Number0是序列号第1、2位，其他依次类推， 寄存器高8位存放序列号第1位； 寄存器低8位存放序列号第2位。 例：0x5353指"SS" | To resolve this you need to check the DCC barcode rule definition document Serial_Number0 is serial number bits 1 and 2, and so on. The high 8 bits of the register hold the serial number bit 1; The low 8 bits of the register store the second bit of the serial number. Example: 0x5353 means "SS"
硬件版本号 | Hardware version number | 044D -- 044E | Hardware_Version0 -- 1 | ASCII |  |  |  |  | R | 硬件版本号0-2（2个，4个ASCII位） | Hardware version number 0-2 (2, 4 ASCII bits) | End-users | [6 empty] | 地址0x044D表示第1、2位。依次类推。 寄存器高8位存放序列号第1位； 寄存器低8位存放序列号第2位。 例：0x5630指"V0",0x3033指"03"，实测：V003 | Address 0x044D means bits 1 and 2. And so on. The high 8 bits of the register hold bit 1 of the sequence number;
通讯芯片 软件版本号 | Communication chip Software version number | 044F | Software_Version_Stage_COM | ASCII |  |  |  |  | R | 通讯芯片软件版本号阶段定义位。 寄存器低8位存放ASCII码。正式版本的默认值为'V'。 | Communication chip software version number phase definition bits. The lower 8 bits of the register hold the ASCII code. The default value for the official version is 'V'. | End-users | [6 empty] | 地址0x044F有'V'、'G'、'I'等版本，均为正式版 0G100003即表示通讯芯片软件版本号为G100003 例1：地址0x044F读取的0x3047表示"0G" 例2：地址0x0450读取的0x3130表示"10" 例3：地址0x0451读取的0x3030表示"00" | Address 0x044F has versions 'V', 'G', 'I', etc., all of which are official versions 0G100003 means that the communication chip software version number is G100003 Example 1: 0x3047 read at address 0x044F means "0G" Example 2: 0x3130 read at address 0x0450 means "10" Example 3: 0x3030 read at address 0x0451 means "00"
|  | 0450 | Software_Version_Major_COM | ASCII |  |  |  |  | R | 通讯芯片软件主版本号。 同一个系统中所有芯片主版本号必须一致，否则视为系统故障。 寄存器高8位存放高位数字； 寄存器低8位存放低位数字。 | Communication chip software major version number. All chip master version numbers in the same system must be the same, otherwise it is considered a system fault. The high 8 bits of the register hold the high digits; The low 8 bits of the register hold the low digits. | End-users
|  | 0451 | Software_Version_Custom_COM | ASCII |  |  |  |  | R | 通讯芯片软件非标定制版本号。 正标软件此版本号为"00"。同一个系统中所有芯片非标定制版本号必须一致，否则视为系统故障。 寄存器高8位存放高位数字； 寄存器低8位存放低位数字。 | Non-standard custom version number of the communication chip software. This version number of the genuine software is "00". All chips in the same system must have the same non-standard custom version number, otherwise it is considered a system fault. The high 8 bits of the register hold the high digit; The lower 8 bits of the register hold the lower digits. | End-users
|  | 0452 | Software_Version_Minor_COM | ASCII |  |  |  |  | R | 通讯芯片软件子版本号。 寄存器高8位存放高位数字； 寄存器低8位存放低位数字。 例：0x3033指"03" | Communication chip software sub-version number. Register high 8 bits hold high digits; The low 8 bits of the register hold the low digit. Example: 0x3033 means "03" | End-users
主控制器芯片 软件版本号 | Main controller chip-Software version number | 0453 | Software_Version_Stage_Master | ASCII |  |  |  |  | R | 主控制器芯片软件版本号阶段定义位。 寄存器低8位存放ASCII码。正式版本的默认值为'V'。 寄存器高8位存放高位数字； 寄存器低8位存放低位数字。 | Master controller chip software version number phase definition bit.The lower 8 bits of the register hold the ASCII code. The default value for the official version is 'V'.Register high 8 bits holding high digits;The low 8 bits of the register hold the low digits." | End-users | [6 empty] | 地址0x0453可能有其他字符 案例分析请查看通讯芯片软件版本号说明 0V100002即表示主控制器芯片软件版本号为V100002 | Address 0x0453 may have other characters For case analysis please check the communication chip software version number description 0V100002 means that the main controller chip software version number is V100002
|  | 0454 | Software_Version_Major_Master | ASCII |  |  |  |  | R | 主控制器芯片软件主版本号。 同一个系统中所有芯片主版本号必须一致，否则视为系统故障。 寄存器高8位存放高位数字； 寄存器低8位存放低位数字。 | Master controller chip software master version number. All chip master version numbers in the same system must be the same, otherwise it is considered a system fault. The high 8 bits of the register hold the high digit; The low 8 bits of the register hold the low digits. | End-users
|  | 0455 | Software_Version_Custom_Master | ASCII |  |  |  |  | R | 主控制器芯片软件非标定制版本号。 正标软件此版本号为"00"。同一个系统中所有芯片非标定制版本号必须一致，否则视为系统故障。 寄存器高8位存放高位数字； 寄存器低8位存放低位数字。 | Non-standard custom version number of the main controller chip software. This version number of the genuine software is "00". All chips in the same system must have the same non-standard custom version number, otherwise it is considered a system fault. The high 8 bits of the register hold the high digit; The lower 8 bits of the register hold the lower digits. | End-users
|  | 0456 | Software_Version_Minor_Master | ASCII |  |  |  |  | R | 主控制器芯片软件子版本号。 寄存器高8位存放高位数字； 寄存器低8位存放低位数字。 | Master controller chip software sub-version number. Register high 8 bits hold high digits; Register low 8 bits hold low digits. | End-users
副控制器芯片 软件版本号 | Sub-controller chips-Software version number | 0457 | Software_Version_Stage_Slave | ASCII |  |  |  |  | R | 副控制器芯片软件版本号阶段定义位。 寄存器低8位存放ASCII码。正式版本的默认值为'V'。 寄存器高8位存放高位数字； 寄存器低8位存放低位数字。 | Sub-controller chip software version number phase definition bits. The low 8 bits of the register hold the ASCII code. The default value for the official version is 'V'. Register high 8 bits hold high digits; The low 8 bits of the register hold the low digits. | End-users | [6 empty] | 地址0x0457可能有其他字符 案例分析请查看通讯芯片软件版本号说明 0L100000即表示副控制器芯片软件版本号为L100000 | Address 0x0457 may have other characters For case study please check the communication chip software version number description 0L100000 means that the sub-controller chip software version number is L100000
|  | 0458 | Software_Version_Major_Slave | ASCII |  |  |  |  | R | 副控制器芯片软件主版本号。 同一个系统中所有芯片主版本号必须一致，否则视为系统故障。 寄存器高8位存放高位数字； 寄存器低8位存放低位数字。 | Sub-controller chip software major version number. All chip master version numbers in the same system must be the same, otherwise it is considered a system fault. The high 8 bits of the register hold the high digits; The low 8 bits of the register hold the low digits. | End-users
|  | 0459 | Software_Version_Custom_Slave | ASCII |  |  |  |  | R | 副控制器芯片软件非标定制版本号。 正标软件此版本号为"00"。同一个系统中所有芯片非标定制版本号必须一致，否则视为系统故障。 寄存器高8位存放高位数字； 寄存器低8位存放低位数字。 | Non-standard custom version number of the sub-controller chip software. This version number of the positive standard software is "00". All chip non-standard custom version numbers in the same system must be the same, otherwise it is considered a system fault. The high 8 bits of the register hold the high digit; The lower 8 bits of the register hold the lower digits. | End-users
|  | 045A | Software_Version_Minor_Slave | ASCII |  |  |  |  | R | 副控制器芯片软件子版本号。 寄存器高8位存放高位数字； 寄存器低8位存放低位数字。 | Sub-controller chip software sub-version number. Register high 8 bits hold high digits; Register low 8 bits holds low digits. | End-users
安规库 版本号 | Safety Library Version number | 045B | Safety_Version_Major | U16 |  |  |  |  | R | 安规库主版本号 例：0x3036指06主版本 | Security library major version number Example: 0x3036 refers to 06 major version | End-users | [6 empty] | 实测：安规版本为608 数据按U16进行存储 按块读是ASCII码，单寄存器读是U16 单寄存器读取时是0x0006、0x0008表示0608 | Actual test: Safety version 608 Data is stored by U16 Read by block is ASCII, single register read is U16 Single register read is 0x0006, 0x0008 for 0608
|  | 045C | Safety_version_Minor | U16 |  |  |  |  | R | 安规库子版本号 例：0x3038指08子版本 | Safety library sub-version number Example: 0x3038 refers to sub-version 08 | End-users
BOOT版本号 | BOOT version number | 045D | Boot_Version_COM | U16 |  |  |  |  | R | 通讯板的BOOT版本号 | BOOT version number of the communication board | End-users
|  | 045E | Boot_Version_Master | U16 |  |  |  |  | R | 主DSP的BOOT版本号 | BOOT version number of the main DSP | End-users
|  | 045F | Boot_Version_Slave | U16 |  |  |  |  | R | 副DSP的BOOT版本号 | BOOT version number of the secondary DSP | End-users
安规认证 相关版本号 | Safety certification-Relevant version number | 0460 | Safety_Firmware_Version_Stage | ASCII |  |  |  |  | R | 安规认证软件版本号阶段定义位。 寄存器低8位存放ASCII码。正式版本的默认值为'V'。 寄存器高8位存放高位数字； 寄存器低8位存放低位数字。 | Phase definition bits of the safety certification software version number. The lower 8 bits of the register hold the ASCII code. The default value for the official version is 'V'. Register high 8 bits holding high digits; The low 8 bits of the register hold the low digit. | End-users | [6 empty] | 案例分析请查看通讯芯片软件版本号说明 0V000001即表示安规软件认证版本号为V000001 | For case studies please see the communication chip software version number description 0V000001 means that the safety software certification version number is V000001
|  | 0461 | Safety_Firmware_Version_Major | ASCII |  |  |  |  | R | 安规认证软件主版本号。 同一个系统中所有芯片主版本号必须一致，否则视为系统故障。 寄存器高8位存放高位数字； 寄存器低8位存放低位数字。 | Safety certified software master version number. All chip master version numbers in the same system must be the same, otherwise it is considered a system fault. The high 8 bits of the register hold the high digit; The lower 8 bits of the register hold the lower digits. | End-users
|  | 0462 | Safety_Firmware_Version_Custom | ASCII |  |  |  |  | R | 安规认证软件非标定制版本号。 正标软件此版本号为"00"。同一个系统中所有芯片非标定制版本号必须一致，否则视为系统故障。 寄存器高8位存放高位数字； 寄存器低8位存放低位数字。 | Non-standard custom version number for safety certified software. This version number of the genuine standard software is "00". All chips in the same system must have the same non-standard custom version number, otherwise it is considered a system fault. The high 8 bits of the register hold the high digit; The lower 8 bits of the register hold the lower digits. | End-users
|  | 0463 | Safety_Firmware_Version_Minor | ASCII |  |  |  |  | R | 安规认证软件子版本号。 寄存器高8位存放高位数字； 寄存器低8位存放低位数字。 | Safety certified software sub-version number. Register high 8 bits hold high digits; Register low 8 bits holds low digits. | End-users
|  | 0464 | Safety_Hardware_Version0 | ASCII |  |  |  |  | R | 安规认证硬件版本号第1、2位。 寄存器高8位存放序列号第1位； 寄存器低8位存放序列号第2位。 | Safety certified hardware version number bits 1 and 2. Register high 8 bits holds serial number bit 1; Register low 8 bits holds serial number bit 2. | End-users | [6 empty] | 案例分析请查看硬件版本号说明 实测：安规硬件认证版本号为V201 | See hardware version number description for case study Actual test: safety-compliant hardware certification version number V201
|  | 0465 | Safety_Hardware_Version1 | ASCII |  |  |  |  | R | 安规认证硬件版本号第3、4位。 寄存器高8位存放序列号第3位； 寄存器低8位存放序列号第4位。 | Safety certified hardware version number bits 3 and 4. Register high 8 bits holds serial number bit 3; Register low 8 bits holds serial number bit 4. | End-users
AFCI版本号 | AFCI version number | 0466 | Afci_Ver_Firmware | ASCII |  |  |  |  | R | afci固件版本号'V'。 高8位保留； 低8位存放版本号。 | afci firmware version number 'V'. High 8 bits reserved; Lower 8 bits hold the version number. | [7 empty] | 案例分析请查看通讯芯片软件版本号说明 请对照ASCII码翻译查看 | For case studies, please check the software version number of the communication chip Please check against ASCII code translation
|  | 0467 | Afci_Ver_Sft | ASCII |  |  |  |  | R | afci软件版本。 高8位存放第1位； 低8位存放第2位。 | afci software version. High 8 bits hold bit 1; Low 8 bits hold bit 2.
|  | 0468 | Afci_Ver_Hard | ASCII |  |  |  |  | R | afci硬件版本 高8位存放第1位； 低8位存放第2位。 | afci hardware version. High 8 bits hold bit 1; Low 8 bits hold bit 2.
|  | 0469 | Afci_Srs_Hard | ASCII |  |  |  |  | R | afci硬件序列号。 高8位存放第1位； 低8位存放第2位。 | afci hardware serial number. High 8 bits hold bit 1; Low 8 bits hold bit 2.
|  | 046A | Afci_Ver_Com | ASCII |  |  |  |  | R | afci通信版本。 高8位存放第1位； 低8位存放第2位。 | afci communication version. High 8 bits hold bit 1; Low 8 bits hold bit 2.
安规文件包 版本号 | Safety documentation package-Version number | 046B | Safety_Package_Version0 | ASCII |  |  |  |  | R | 安规文件包版本号第1、2位。 寄存器高8位存放序列号第1位； 寄存器低8位存放序列号第2位。 | anci file package version number bits 1 and 2. Register high 8 bits holds serial number bit 1; Register low 8 bits holds serial number bit 2. | [7 empty] | 案例分析请查看通讯芯片软件版本号说明请对照ASCII码翻译查看 | For case studies please check the communication chip software version number description please check against the ASCII code translation
|  | 046C | Safety_Package_Version1 | ASCII |  |  |  |  | R | 安规文件包版本号第3、4位。 寄存器高8位存放序列号第3位； 寄存器低8位存放序列号第4位。 | Bit 3 and 4 of the version number of the safety file package. Register high 8 bits to hold serial number bit 3; Register low 8 bits holds serial number bit 4.
|  | 046D -- 046F | [7 empty] | 预留 | Reserved
机器序列号 2-2 | Machine serial number 2-2 | 0470 -- 0471 | Serial_Number8 -- 9 | ASCII |  |  |  |  | R | 机器序列号Serial_Number8-9。 表示第17-20位，第1-16位在寄存器地址0x0445 | Machine serial number Serial_Number8-9. Indicates bits 17-20, bits 1-16 in register address 0x0445 | End-users | [6 empty] | 序列号第15-20位在20位序列号使用，14位序列号不使用 寄存器0x0470高8位存放序列号第17位； 寄存器0x0470低8位存放序列号第18位。 | Serial number bits 15-20 are used in 20-bit serial number, 14-bit serial number is not used register 0x0470 high 8 bits holds the 17th bit of the serial number; Register 0x0470 low 8 bits holds serial number bit 18.
|  | 0472 -- 0476 | Serial_Number11_Rsvd0 -- 4 | ASCII |  |  |  |  | R | 预留0-4（5个） | Reserved 0-4 (of 5)
状态信息表 | Status information sheet | 0477 -- 047F | State1 -- 9 | U16 |  |  |  |  | R | 状态信息表1-9（9个）。 记录逆变器的状态信息 | Status information table 1-9 (9) Records the status information of the inverter | End-users | [6 empty] | 对应状态信息查看此表格的另外一张工作表“状态信息表” | For the corresponding status information see the other worksheet of this form "Status Information Sheet"
2.2Grid-connected output(0x0480-0x04FF)
|  | 0480 -- 0483 | AddressMask_Realtime_GridOutput1 | U64 |  |  |  |  | R | 本地址开始的64个寄存器地址字的掩码区。 参看地址0x0040的说明 | Mask area for the 64 register address words starting at this address. Refer to the description of address 0x0040 | End-users | 00000000 | 0000000F
电网频率 | Grid frequency | 0484 | Frequency_Grid | U16 | 0.01 | Hz |  |  | R | 电网频率。 | Grid frequency. | End-users | [6 empty] | 例：0x138B表示50.03Hz | Example: 0x138B means 50.03Hz
功率数据 | Power data | 0485 | ActivePower_Output_Total | I16 | 0.01 | kW |  |  | R | 总有功功率。 | Total active power. | End-users | [6 empty] | 逆变器的输出功率，放电为正，充电为负 例：0x006A表示1.06KW | Inverter output power, discharging is positive, charging is negative Example: 0x006A means 1.06 KW
|  | 0486 | ReactivePower_Output_Total | I16 | 0.01 | kW |  |  | R | 总无功功率。 | Total reactive power. | End-users | [6 empty] | 用来在设备中建立和维持磁场的电功率，逆变器端超前为正，滞后为负 | Electrical power used to establish and maintain the magnetic field in the device, overrun is positive and hysteresis is negative at the inverter end
|  | 0487 | ApparentPower_Output_Total | I16 | 0.01 | kW |  |  | R | 总视在功率。 | Total apparent power. | End-users | [6 empty] | 逆变器当前电压电流的最大有功功率，放电为正，充电为负 | The maximum active power of the current voltage and current of the inverter, positive for discharging, negative for charging
|  | 0488 | ActivePower_PCC_Total | I16 | 0.01 | kW |  |  | R | 总PCC有功功率。 | Total PCC active power. | End-users | [6 empty] | 能流图电网功率的读取地址，部分机型需要接电表才有数据，卖电为正，买电为负 | Reading address of the grid power of the energy flow diagram, some models need to be connected to a power meter to have data, positive for selling power, negative for buying power
|  | 0489 | ReactivePower_PCC_Total | I16 | 0.01 | kW |  |  | R | 总PCC无功功率。 | Total PCC reactive power. | End-users | [6 empty] | 逆变器端超前为正，滞后为负 | The inverter side is positive for overruns and negative for lags
|  | 048A | ApparentPower_PCC_Total | I16 | 0.01 | kW |  |  | R | 总PCC视在功率。 | Total PCC apparent power. | End-users | [6 empty] | 卖电为正，买电为负 | Positive for selling power, negative for buying power
|  | 048B -- 048C | GridOutput_Rsvd1 -- 2 | [5 empty] | R | 并网输出预留1-2 | Grid connected output reserve 1-2 | End-users
R相并网 实时数据 | R-phase grid connection Real-time data | 048D | Voltage_Phase_R | U16 | 0.1 | V |  |  | R | R相电网电压 | R-phase grid voltage | End-users | [6 empty] | 例：0x093E表示236.6V | Example: 0x093E means 236.6V
|  | 048E | Current_Output_R | U16 | 0.01 | A |  |  | R | R相逆变器输出电流 | Phase R inverter output current | End-users | [6 empty] | 例：0x0049表示0.73A | Example: 0x0049 means 0.73A
|  | 048F | ActivePower_Output_R | I16 | 0.01 | kW |  |  | R | R相逆变器输出有功功率。 | R-phase inverter output active power. | End-users | [6 empty] | 放电为正，充电为负 | Discharge is positive, charge is negative
|  | 0490 | ReactivePower_Output_R | I16 | 0.01 | kW |  |  | R | R相逆变器输出无功功率。 | R phase inverter output reactive power. | End-users | [6 empty] | 逆变器端超前为正，滞后为负 | Inverter side overrun is positive, hysteresis is negative
|  | 0491 | PowerFactor_Output_R | I16 | 0.001 | p.u. |  |  | R | R相功率因数。 | R-phase power factor. | End-users | [6 empty] | 逆变器端超前为正，滞后为负 | Inverter side overrun is positive, hysteresis is negative
|  | 0492 | Current_PCC_R | U16 | 0.01 | A |  |  | R | R相PCC电流。 | R-phase PCC current. | End-users | [6 empty] | 部分机型需要接电表才有数据 | Some models need to be connected to a power meter to get data
|  | 0493 | ActivePower_PCC_R | I16 | 0.01 | kW |  |  | R | R相PCC有功功率 | R-phase PCC active power | End-users | [6 empty] | 逆变器端超前为正，滞后为负 | Positive overrun, negative hysteresis on inverter side
|  | 0494 | ReactivePower_PCC_R | I16 | 0.01 | kW |  |  | R | R相PCC无功功率。 | R-phase PCC reactive power. | End-users
|  | 0495 | PowerFactor_PCC_R | I16 | 0.001 | p.u. |  |  | R | R相PCC功率因数。 | R phase PCC power factor. | End-users | [6 empty] | 逆变器端超前为正，滞后为负 | Positive overrun, negative hysteresis on inverter side
|  | 0496 -- 0497 | R_Rsvd1 -- 2 | [5 empty] | R | R相预留1-2 | Phase R reserved 1-2 | End-users
S相并网 实时数据 | S-phase grid connection Real-time data | 0498 | Voltage_Phase_S | U16 | 0.1 | V |  |  | R | S相电网电压 | Phase S grid voltage | End-users | [6 empty] | 参考上面R相的相关说明 | Refer to the relevant notes for R-phase above
|  | 0499 | Current_Output_S | U16 | 0.01 | A |  |  | R | S相逆变器输出电流 | Phase S inverter output current | End-users
|  | 049A | ActivePower_Output_S | I16 | 0.01 | kW |  |  | R | S相逆变器输出有功功率。 | S phase inverter output active power. | End-users
|  | 049B | ReactivePower_Output_S | I16 | 0.01 | kW |  |  | R | S相逆变器输出无功功率。 | S phase inverter output reactive power. | End-users
|  | 049C | PowerFactor_Output_S | I16 | 0.001 | p.u. |  |  | R | S相功率因数。 | S phase power factor. | End-users
|  | 049D | Current_PCC_S | U16 | 0.01 | A |  |  | R | S相PCC电流 | S phase PCC current | End-users
|  | 049E | ActivePower_PCC_S | I16 | 0.01 | kW |  |  | R | S相PCC有功功率。 | S phase PCC active power. | End-users
|  | 049F | ReactivePower_PCC_S | I16 | 0.01 | kW |  |  | R | S相PCC无功功率。 | S phase PCC reactive power. | End-users
|  | 04A0 | PowerFactor_PCC_S | I16 | 0.001 | p.u. |  |  | R | S相PCC功率因数。 | S phase PCC power factor. | End-users
|  | 04A1 -- 04A2 | S_Rsvd1 -- 2 | [5 empty] | R | S相预留1-2 | S phase reserved 1-2 | End-users
T相并网 实时数据 | T-phase grid connection Real-time data | 04A3 | Voltage_Phase_T | U16 | 0.1 | V |  |  | R | T相电网电压 | Phase T grid voltage | End-users | [6 empty] | 参考上面R相的相关说明 | Refer to the instructions for R-phase above
|  | 04A4 | Current_Output_T | U16 | 0.01 | A |  |  | R | T相逆变器输出电流 | Phase T inverter output current | End-users
|  | 04A5 | ActivePower_Output_T | I16 | 0.01 | kW |  |  | R | T相逆变器输出有功功率。 | T-phase inverter output active power. | End-users
|  | 04A6 | ReactivePower_Output_T | I16 | 0.01 | kW |  |  | R | T相逆变器输出无功功率。 | T-phase inverter output reactive power. | End-users
|  | 04A7 | PowerFactor_Output_T | I16 | 0.001 | p.u. |  |  | R | T相功率因数。 | T-phase power factor. | End-users
|  | 04A8 | Current_PCC_T | U16 | 0.01 | A |  |  | R | T相PCC电流。 | T-phase PCC current. | End-users
|  | 04A9 | ActivePower_PCC_T | I16 | 0.01 | kW |  |  | R | T相PCC有功功率。 | T-phase PCC active power. | End-users
|  | 04AA | ReactivePower_PCC_T | I16 | 0.01 | kW |  |  | R | T相PCC无功功率。 | T-phase PCC reactive power. | End-users
|  | 04AB | PowerFactor_PCC_T | I16 | 0.001 | p.u. |  |  | R | T相PCC功率因数。 | T-phase PCC power factor. | End-users
|  | 04AC -- 04AD | T_Rsvd1 -- 2 | [5 empty] | R | T相预留1-2 | T-phase reserved for 1-2 | End-users
其他并网 实时数据 | Other grid connections-Real-time data | 04AE | ActivePower_PV_Ext | U16 | 0.01 | kW |  |  | R | 外部发电功率 | External power generation | End-users | [6 empty] | 读出来的数乘精度即为最终数据 | The readout multiplied by the accuracy is the final data
|  | 04AF | ActivePower_Load_Sys | U16 | 0.01 | kW |  |  | R | 系统总负载功率 | Total system load power | End-users | [6 empty] | 需要接负载，能流图负载功率的读取地址 | The load needs to be connected and the address for reading the load power of the energy flow diagram
|  | 04B0 | Voltage_Phase_L1N | U16 | 0.1 | V |  |  | R | 电网L1对N电压有效值 | Grid L1 to N voltage RMS | End-users
|  | 04B1 | Current_Output_L1N | U16 | 0.01 | A |  |  | R | L1输出电流有效值 | L1 output current RMS | End-users
|  | 04B2 | ActivePower_Output_L1N | I16 | 0.01 | kW |  |  | R | L1线上输出有功功率 | Active power output on L1 line | End-users
|  | 04B3 | Current_PCC_L1N | U16 | 0.01 | A |  |  | R | L1线上CT电流有效值 | RMS CT current on line L1 | End-users
|  | 04B4 | ActivePower_PCC_L1N | I16 | 0.01 | kW |  |  | R | L1线上PCC有功功率 | PCC active power on line L1 | End-users
|  | 04B5 | Voltage_Phase_L2N | U16 | 0.1 | V |  |  | R | 电网L2对N电压有效值 | Grid L2 RMS voltage to N | End-users
|  | 04B6 | Current_Output_L2N | U16 | 0.01 | A |  |  | R | L2输出电流有效值 | RMS L2 output current | End-users
|  | 04B7 | ActivePower_Output_L2N | I16 | 0.01 | kW |  |  | R | L2线上输出有功功率 | Active power output on line L2 | End-users
|  | 04B8 | Current_PCC_L2N | U16 | 0.01 | A |  |  | R | L2线上CT电流有效值 | RMS CT current on L2 | End-users
|  | 04B9 | ActivePower_PCC_L2N | I16 | 0.01 | kW |  |  | R | L2线上PCC有功功率 | PCC active power on line L2 | End-users
|  | 04BA | Voltage_Line_L1 | U16 | 0.1 | V |  |  | R | L1线电压：R/S相之间的电压 | Line voltage L1: voltage between phases R/S | End-users | [6 empty] | 三相机型才有此功能,例：0x1014表示411.6V | This function is only available for three-phase models, e.g. 0x1014 means 411.6V
|  | 04BB | Voltage_Line_L2 | U16 | 0.1 | V |  |  | R | L2线电压：S/T相之间的电压 | L2 line voltage: voltage between S/T phases | End-users | [6 empty] | 参考L1线电压 | Reference L1 line voltage
|  | 04BC | Voltage_Line_L3 | U16 | 0.1 | V |  |  | R | L3线电压：T/R相之间的电压 | Line L3 voltage: voltage between phases T/R | End-users
|  | 04BD | Power_Factor | I16 | 0.001 | p.u. |  |  | R | 总功率因数。 | Total power factor. | End-users | [6 empty] | 逆变器端超前为正，滞后为负 | Overrun is positive, hysteresis is negative at the inverter end
2.3Off-grid output(0x0500-0x057F)
|  | 0500 -- 0503 | AddressMask_Realtime_EmergencyOutput1 | U64 |  |  |  |  | R | 本地址开始的64个寄存器地址字的掩码区。 参看地址0x0040的说明 | Mask area for the 64 register address words starting at this address. Refer to the description of address 0x0040 | End-users | 00000000 | 0000000F
负载功率 | Load power | 0504 | ActivePower_Load_Total | I16 | 0.01 | kW |  |  | R | 负载有功功率。 | Load active power. | End-users | [6 empty] | 负载消耗为正，回馈为负。 | Load consumption is positive, feedback is negative.
|  | 0505 | ReactivePower_Load_Total | I16 | 0.01 | kW |  |  | R | 负载无功功率 | Load reactive power | End-users
|  | 0506 | ApparentPower_Load_Total | I16 | 0.01 | kW |  |  | R | 负载视在功率。 | Load apparent power. | End-users | [6 empty] | 负载消耗为正，回馈为负。 | Load consumption is positive, feedback is negative.
输出电压频率 | Output voltage frequency | 0507 | Frequency_Output | U16 | 0.01 | Hz |  |  | R | 输出电压频率 | Output voltage frequency | End-users | [6 empty] | 逆变器输出的电压频率 | The voltage frequency of the inverter output
|  | 0508 -- 0509 | ESOutput_Rsvd1 -- 2 | [5 empty] | R | 离网总输出预留1-2 | Off-grid total output reserve 1-2 | End-users
R相离网 实时数据 | R-phase off-grid Real-time data | 050A | Voltage_Output_R | U16 | 0.1 | V |  |  | R | R相逆变器输出电压 | R-phase inverter output voltage | End-users
|  | 050B | Current_Load_R | I16 | 0.01 | A |  |  | R | R相负载电流 | Phase R load current | End-users | [6 empty] | R相与负载的电流 | R-phase with load current
|  | 050C | ActivePower_Load_R | I16 | 0.01 | kW |  |  | R | R相负载有功功率。 | R-phase load active power. | End-users | [6 empty] | 单相负载有功功率，负载消耗为正，回馈为负。 | Active power of single-phase load with positive load consumption and negative feed-back
|  | 050D | ReactivePower_Load_R | I16 | 0.01 | kW |  |  | R | R相负载无功功率。 | R-phase load reactive power. | End-users | [6 empty] | 逆变器端超前为正，滞后为负 | Inverter side overrun is positive, hysteresis is negative
|  | 050E | ApparentPower_Load_R | I16 | 0.01 | kVA |  |  | R | R相负载视在功率。 | R-phase load apparent power. | End-users | [6 empty] | 负载消耗为正，回馈为负。 | Positive for load consumption, negative for return
|  | 050F | LoadPeakRatio_R | U16 | 0.01 | p.u. |  |  | R | R相负载峰值比 | R phase load peak ratio | End-users
|  | 0510 | Voltage_Load_R | U16 | 0.1 | V |  |  | R | R相应急负载电压 | R corresponding acute load voltage | End-users
|  | 0511 | ESR_Rsvd2 | [5 empty] | R | R相预留2 | R phase reserve 2 | End-users
S相离网 实时数据 | S-phase off-grid Real-time data | 0512 | Voltage_Output_S | U16 | 0.1 | V |  |  | R | S相逆变器输出电压 | Phase S inverter output voltage | End-users | [6 empty] | 参考上面R相的相关说明 | Refer to the relevant note for phase R above
|  | 0513 | Current_Load_S | I16 | 0.01 | A |  |  | R | S相负载电流 | S phase load current | End-users
|  | 0514 | ActivePower_Load_S | I16 | 0.01 | kW |  |  | R | S相负载有功功率。 | S phase load active power. | End-users
|  | 0515 | ReactivePower_Load_S | I16 | 0.01 | kW |  |  | R | S相负载无功功率。 | S phase load reactive power. | End-users
|  | 0516 | ApparentPower_Load_S | I16 | 0.01 | kVA |  |  | R | S相负载视在功率。 | S phase load apparent power. | End-users
|  | 0517 | LoadPeakRatio_S | U16 | 0.01 | p.u. |  |  | R | S相负载峰值比 | S phase load peak ratio | End-users
|  | 0518 | Voltage_Load_S | U16 | 0.1 | V |  |  | R | S相应急负载电压 | S phase corresponding acute load voltage | End-users
|  | 0519 | ESS_Rsvd2 | [5 empty] | R | S相预留2 | S phase reserve 2 | End-users
T相离网 实时数据 | T-phase off-grid Real-time data | 051A | Voltage_Output_T | U16 | 0.1 | V |  |  | R | T相逆变器输出电压 | T-phase inverter output voltage | End-users | [6 empty] | 参考上面R相的相关说明 | Refer to the description of phase R above
|  | 051B | Current_Load_T | I16 | 0.01 | A |  |  | R | T相负载电流 | T phase load current | End-users
|  | 051C | ActivePower_Load_T | I16 | 0.01 | kW |  |  | R | T相负载有功功率。 | T phase load active power. | End-users
|  | 051D | ReactivePower_Load_T | I16 | 0.01 | kW |  |  | R | T相负载无功功率。 | T phase load reactive power. | End-users
|  | 051E | ApparentPower_Load_T | I16 | 0.01 | kVA |  |  | R | T相负载视在功率。 | T-phase load apparent power. | End-users
|  | 051F | LoadPeakRatio_T | U16 | 0.01 | p.u. |  |  | R | T相负载峰值比 | T phase load peak ratio | End-users
|  | 0520 | Voltage_Load_T | U16 | 0.1 | V |  |  | R | T相应急负载电压 | T corresponding acute load voltage | End-users
|  | 0521 | EST_Rsvd2 | [5 empty] | R | T相预留2 | T phase reserved 2 | End-users
其他离网 实时数据 | "Other off-grid Real Time Data" | 0522 | Voltage_Output_L1N | U16 | 0.1 | V |  |  | R | 逆变L1对N电压有效值 | Inverter L1 to N voltage RMS | End-users
|  | 0523 | Current_Load_L1N | I16 | 0.01 | A |  |  | R | L1负载电流有效值 | L1 load current RMS | End-users
|  | 0524 | ActivePower_Load_L1N | I16 | 0.01 | kW |  |  | R | 负载L1对N有功功率 | Load L1 to N active power | End-users
|  | 0525 | Voltage_Output_L2N | U16 | 0.1 | V |  |  | R | 逆变L2对N电压有效值 | Inverter L2 to N voltage RMS | End-users
|  | 0526 | Current_Load_L2N | I16 | 0.01 | A |  |  | R | L2负载电流有效值 | L2 load current RMS | End-users
|  | 0527 | ActivePower_Load_L2N | I16 | 0.01 | kW |  |  | R | 负载L2对N有功功率 | Load L2 to N active power | End-users
2.4PV input(0x0580-0x05FF)
|  | 0580 -- 0583 | AddressMask_Realtime_Input_PV1 | U64 |  |  |  |  | R | 本地址开始的64个寄存器地址字的掩码区。 参看地址0x0040的说明 | Mask area for the 64 register address words starting at this address. Refer to the description of address 0x0040 | End-users | 00000000 | 0000000F
PV1-16 电压 电流 功率 数据 | PV1-16 Voltage Current Power Data | 0584 -- 05B1 | Voltage_PV1 -- 16 | U16 | 0.1 | V |  |  | R | 第1-16路PV电压（16个）。 地址从0x0584开始，每路间隔3个地址。 | PV voltages (16) for channels 1-16. Addresses start at 0x0584 and are spaced 3 addresses apart each way. | End-users | [6 empty] | PV的路数和具体机型有关。 读出来的数乘精度即为最终数据 例1：地址0x0584读取：0x0906为231V 例2：地址0x0585读取：0x01BB为4.43A 例3：地址0x0586读取：0x0066为1.02KW 其他参考第1路PV电压、电流和功率 | The number of ways of PV is related to the specific model. The number read out multiplied by the precision is the final data Example 1: Read at address 0x0584: 0x0906 for 231V Example 2: Address 0x0585 read: 0x01BB for 4.43A Example 3: Address 0x0586 reads: 0x0066 for 1.02KW Other references to PV voltage, current and power for circuit 1
|  | 0585 -- 05B2 | Current_PV1 -- 16 | U16 | 0.01 | A |  |  | R | 第1-16路PV电流。 地址从0x0585开始，每路间隔3个地址。 | PV currents for channels 1-16. Addresses start at 0x0585 and are spaced 3 addresses apart each way. | End-users
|  | 0586 -- 05B3 | Power_PV1 -- 16 | U16 | 0.01 | kW |  |  | R | 第1-16路PV功率。 地址从0x0586开始，每路间隔3个地址。 | 1st-16th PV Power. Addresses start at 0x0586 and are spaced 3 addresses apart each way. | End-users
|  | 05B4 -- 05B6 | [7 empty] | 预留 | Reserved
|  | 05C0 -- 05C3 | AddressMask_Realtime_Input_PV2 | U64 |  |  |  |  | R | 本地址开始的64个寄存器地址字的掩码区。 参看地址0x0040的说明 | Mask area for 64 register address words starting at this address. Refer to the description of address 0x0040 | End-users | 00000000 | 0000000F
总PV功率 | Total PV power | 05C4 | Power_PV_Total | U16 | 0.1 | kW |  |  | R | 总PV功率。 | Total PV power. | End-users | [6 empty] | 所有PV功率之和,读出来的数乘精度即为最终数据 例：0x0007表示0.7kw | The sum of all PV power, the number read out multiplied by the precision is the final data Example: 0x0007 means 0.7kw
2.5Battery input(0x0600-0x067F)
|  | 0600 -- 0603 | AddressMask_Realtime_Input_Bat1 | U64 |  |  |  |  | R | 本地址开始的64个寄存器地址字的掩码区。 参看地址0x0040的说明 | Mask area for the 64 register address words starting at this address. Refer to the description of address 0x0040 | End-users | 00000000 | 0000000F
第1-8路电池组 数据 | Battery pack 1-8 Data | 0604 -- 0635 | Voltage_Bat1 -- 8 | U16 | 0.1 | V |  |  | R | 第1-8路电池组电压。 | Battery pack voltage for channels 1-8. | End-users | [6 empty] | 电池路数与具体机型有关 每路间隔7个地址。 读出来的数乘精度即为最终数据 充放电电流：充电为正，放电为负 例：0x016C表示36.4V | The number of battery circuits is related to the specific model Each road is spaced by 7 addresses. The number read out multiplied by the accuracy is the final data Charging and discharging current: charging is positive, discharging is negative Example: 0x016C means 36.4V
|  | 0605 -- 0636 | Current_Bat1 -- 8 | I16 | 0.01 | A |  |  | R | 第1-8路电池组充放电电流。 | Channels 1-8 battery pack charge/discharge current. | End-users
|  | 0606 -- 0637 | Power_Bat1 -- 8 | I16 | 0.01 | kW |  |  | R | 第1-8路电池组充放电功率。 | Battery pack charge/discharge power for channels 1-8. | End-users
|  | 0607 -- 0638 | Temperature_Env_Bat1 -- 8 | I16 | 1 | ℃ |  |  | R | 第1-8路电池组环境温度。 | Ambient temperature of battery pack 1-8. | End-users | [6 empty] | 电池外围温度，负数表示零下温度。 每路间隔7个地址。 | Battery peripheral temperature, negative numbers indicate sub-zero temperature. 7 addresses per circuit interval.
|  | 0608 -- 0639 | SOC_Bat1 -- 8 | U16 | 1 | % |  |  | R | 第1-8路电池组SOC。 | Battery pack SOC 1-8. | End-users | [6 empty] | 电池电量 每路间隔7个地址。 | Battery level 7 addresses per circuit interval.
|  | 0609 -- 063A | SOH_Bat1 -- 8 | U16 | 1 | % |  |  | R | 第1-8路电池组SOH。 | 1-8th battery pack SOH. | End-users | [6 empty] | 当前电池相对于新电池存储电能的能力 每路间隔7个地址。 | Current battery capacity to store power relative to new battery 7 addresses per circuit interval.
|  | 060A -- 063B | ChargeCycle_Bat1 -- 8 | U16 | 1 | cycle |  |  | R | 第1-8路电池组循环次数。 | Number of cycles of battery pack 1-8. | End-users | [6 empty] | 电池充放电循环次数 每路间隔7个地址。 | Number of battery charge and discharge cycles 7 addresses per circuit interval.
|  | 063C -- 063F | [7 empty] | 预留 | Reserved
|  | 0640 -- 0643 | AddressMask_Realtime_Input_Bat2 | U64 |  |  |  |  | R | 本地址开始的64个寄存器地址字的掩码区。 参看地址0x0040的说明 | Mask area for the 64 register address words starting at this address. Refer to the description of address 0x0040 | End-users | 00000000 | 0000000F
第9-12路电池组 数据 | Battery pack 9-12 Data | 0644 -- 0659 | Voltage_Bat9 -- 12 | U16 | 0.1 | V |  |  | R | 第9-12路电池组电压。 | Battery pack voltage for circuits 9-12. | End-users | [6 empty] | 电池路数与具体机型有关 案例参考第1路电池组说明 每路间隔7个地址 | The number of battery circuits relates to the specific model Case reference 1st battery pack description 7 addresses per circuit interval.
|  | 0645 -- 065A | Current_Bat9 -- 12 | I16 | 0.01 | A |  |  | R | 第9-12路电池组充放电电流。 | Channels 9-12 battery pack charge/discharge current. | End-users
|  | 0646 -- 065B | Power_Bat9 -- 12 | I16 | 0.01 | kW |  |  | R | 第9-12路电池组充放电功率。 | Channels 9-12 battery pack charge/discharge power. | End-users
|  | 0647 -- 065C | Temperature_Env_Bat9 -- 12 | I16 | 1 | ℃ |  |  | R | 第9-12路电池组环境温度。 | Road 9-12 battery pack ambient temperature. | End-users
|  | 0648 -- 065D | SOC_Bat9 -- 12 | U16 | 1 | % |  |  | R | 第9-12路电池组SOC | Rd 9-12 battery pack SOC | End-users
|  | 0649 -- 065E | SOH_Bat9 -- 12 | U16 | 1 | % |  |  | R | 第9-12路电池组SOH | Rd 9-12 battery pack SOH | End-users
|  | 064A --065F | ChargeCycle_Bat9 -- 12 | U16 | 1 | cycle |  |  | R | 第9-12路电池组循环次数 | No. of cycles of 9-12 way battery pack | End-users
|  | 0660 -- 0666 | [7 empty] | 预留 | Reserved
电池组 其他数据 | Battery pack Other data | 0667 | Power_Bat_Total | I16 | 0.1 | kW |  |  | R | 总电池充放电功率。充电为正，放电为负 | Total battery charging and discharging power. Charging is positive, discharging is negative | End-users
|  | 0668 | SOC_Bat_Average | U16 | 1 | % |  |  | R | 汇总电池组SOC的平均值 | Average of total battery pack SOC | End-users | [6 empty] | 平均电量 | Average charge capacity
|  | 0669 | SOH_Bat | U16 | 1 | % |  |  | R | 汇总电池组SOH | Aggregate battery pack SOH | End-users | [6 empty] | 当前电池相对于新电池存储电能的能力 | Capacity of the current battery to store electrical energy relative to the new battery
|  | 066A | CurrentBattery_num | U16 | 1 |  |  |  | R | 实时电池路数 | Real-time battery path count
2.6Amount of electricity(0x0680-0x06BF)
|  | 0680 -- 0683 | AddressMask_Realtime_ElectricityStatistics1 | U64 |  |  |  |  | R | 本地址开始的64个寄存器地址字的掩码区。 参看地址0x0040的说明 | Mask area for the 64 register address words starting at this address. Refer to the description of address 0x0040 | End-users | 00000000 | 0000000F
电量数据 | Electricity data | 0684 -- 0685 | PV_Generation_Today | U32 | 0.01 | kWh |  |  | R | 当日发电量 | Power generation for the day | End-users | [6 empty] | 低地址为高位，高地址为低位，读出来的数乘精度即为最终数据，例：0x0000 0x00EF表示2.39KWh | The low address is the high bit, the high address is the low bit, the number read out multiplied by the precision is the final data, example: 0x0000 0x00EF means 2.39KWh
|  | 0686 -- 0687 | PV_Generation_Total | U32 | 0.1 | kWh |  |  | R | 总发电量 | Total power generation | End-users | [6 empty] | 低地址为高位，高地址为低位，读出来的数乘精度即为最终数据，例：0x0000 0x0017表示2.3KWh | The low address is high, the high address is low, the number read out multiplied by the precision is the final data, example: 0x0000 0x0017 means 2.3KWh
|  | 0688 -- 0689 | Load_Consumption_Today | U32 | 0.01 | kWh |  |  | R | 当日负载耗电量 | Load power consumption for the day | End-users | [6 empty] | 低地址为高位，高地址为低位 读出来的数乘精度即为最终数据 案例请参考0x0684与0x0685地址 | The low address is the high bit, the high address is the low bit The multiplication accuracy read out is the final data Please refer to 0x0684 and 0x0685 addresses for examples
|  | 068A -- 068B | Load_Consumption_Total | U32 | 0.1 | kWh |  |  | R | 总负载耗电量 | Total load power consumption | End-users
|  | 068C -- 068D | Energy_Purchase_Today | U32 | 0.01 | kWh |  |  | R | 当日买电量 | Power bought for the day | End-users
|  | 068E -- 068F | Energy_Purchase_Total | U32 | 0.1 | kWh |  |  | R | 总买电量 | Total power bought | End-users
|  | 0690 -- 0691 | Energy_Selling_Today | U32 | 0.01 | kWh |  |  | R | 当日卖电量 | Power sold on the day | End-users
|  | 0692 -- 0693 | Energy_Selling_Total | U32 | 0.1 | kWh |  |  | R | 总卖电量 | Total power sold | End-users
|  | 0694 -- 0695 | Bat_Charge_Today | U32 | 0.01 | kWh |  |  | R | 当日电池充电量 | Daily Battery Charging | End-users
|  | 0696 -- 0697 | Bat_Charge_Total | U32 | 0.1 | kWh |  |  | R | 总电池充电量 | Total Battery Charging | End-users
|  | 0698 -- 0699 | Bat_Discharge_Today | U32 | 0.01 | kWh |  |  | R | 当日电池放电量 | Daily Battery Discharge | End-users
|  | 069A -- 069B | Bat_Discharge_Total | U32 | 0.1 | kWh |  |  | R | 总电池放电量 | Total Battery Discharge | End-users
当年当月 电量数据 | Current month of the year Electricity data | 069C -- 069D | PV_Generation_Month | U32 | 0.1 | kWh |  |  | R | 本月发电量 | Electricity generated this month | End-users
|  | 069E -- 069F | PV_Generation_Year | U32 | 0.1 | kWh |  |  | R | 本年发电量 | Current year's electricity generation | End-users
|  | 06A0 -- 06A1 | Load_Consumption_Month | U32 | 0.1 | kWh |  |  | R | 本月负载耗电量 | Load consumption for the month | End-users
|  | 06A2 -- 06A3 | Load_Consumption_Year | U32 | 0.1 | kWh |  |  | R | 本年负载耗电量 | Current year's load power consumption | End-users
|  | 06A4 -- 06A5 | Energy_Purchase_Month | U32 | 0.1 | kWh |  |  | R | 本月买电量 | Power bought this month | End-users
|  | 06A6 -- 06A7 | Energy_Purchase_Year | U32 | 0.1 | kWh |  |  | R | 本年买电量 | Electricity bought this year | End-users
|  | 06A8 -- 06A9 | Energy_Selling_Month | U32 | 0.1 | kWh |  |  | R | 本月卖电量 | Electricity sold during the month | End-users
|  | 06AA -- 06AB | Energy_Selling_Year | U32 | 0.1 | kWh |  |  | R | 本年卖电量 | Electricity sold this year | End-users
|  | 06AC -- 06AD | Bat_Charge_Month | U32 | 0.1 | kWh |  |  | R | 本月电池充电量 | Battery charge for the month | End-users
|  | 06AE -- 06AF | Bat_Charge_Year | U32 | 0.1 | kWh |  |  | R | 本年电池充电量 | Battery charge this year | End-users
|  | 06B0 -- 06B1 | Bat_Discharge_Month | U32 | 0.1 | kWh |  |  | R | 本月电池放电量 | Battery discharge for the month | End-users
|  | 06B2 -- 06B3 | Bat_Discharge_Year | U32 | 0.1 | kWh |  |  | R | 本年电池放电量 | Current year's battery discharge | End-users
2.7Internal information0x06C0-0x06FF)
|  | 06C0 -- 06C3 | AddressMask_Realtime_ClassifiedInfo1 | U64 |  |  |  |  | R | 本地址开始的64个寄存器地址字的掩码区。 参看地址0x0040的说明 | Mask area for the 64 register address words starting at this address. Refer to the description of address 0x0040 | Installers | 00000000 | 0000000F
漏电流 | Leakage current | 06C4 | GFCI | U16 | 1 | mA |  |  | R | 漏电流 | Leakage current | Installers | [6 empty] | 例：0x0005表示5mA | Example: 0x0005 means 5mA
平衡电流 | Balance current | 06C5 | Current_Bus_Balance | I16 | 0.01 | A |  |  | R | 平衡电流 | Balance current | Installers | [6 empty] | 注：实现三相平衡 | Note: To achieve a balanced three-phase
直流分量 | DC component | 06C6 | DCI_R | I16 | 1 | mA |  |  | R | R相电流直流分量 | DC component of R-phase current | Installers
|  | 06C7 | DCI_S | I16 | 1 | mA |  |  | R | S相电流直流分量 | S phase current DC component | Installers
|  | 06C8 | DCI_T | I16 | 1 | mA |  |  | R | T相电流直流分量 | Phase T current DC component | Installers
|  | 06C9 | DCV_R | I16 | 1 | mV |  |  | R | R相电压直流分量 | DC component of phase R voltage | Installers
|  | 06CA | DCV_S | I16 | 1 | mV |  |  | R | S相电压直流分量 | DC component of phase S voltage | Installers
|  | 06CB | DCV_T | I16 | 1 | mV |  |  | R | T相电压直流分量 | DC component of T-phase voltage | Installers
BUS电压信息 BuckBoost电流 | BUS voltage information BuckBoost current | 06CC | Voltage_Bus | U16 | 0.1 | V |  |  | R | 总BUS电压 | Total BUS voltage | Installers | [6 empty] | 母线电压，逆变器会将PV的输入电压升压到BUS电压，达到逆变要求，再进行逆变 | bus voltage, the inverter will step up the input voltage of the PV to BUS voltage to reach the inverter requirement, and then carry out the inverter
|  | 06CD | Voltage_Bus_P | U16 | 0.1 | V |  |  | R | BUS正电压 | BUS positive voltage | Installers | [6 empty] | bus+,对地电压为正 | bus+,the voltage to ground is positive
|  | 06CE | Voltage_Bus_N | U16 | 0.1 | V |  |  | R | BUS负电压 | BUS negative voltage | Installers | [6 empty] | bus-,对地电压为负 | bus-, negative voltage to ground
|  | 06CF | Voltage_Bus_LLC | U16 | 0.1 | V |  |  | R | LLC Bus电压 | LLC Bus Voltage | Installers
|  | 06D0 | Current_BuckBoost | I16 | 0.01 | A |  |  | R | BuckBoost电流 | BuckBoost current | Installers
|  | 06D1 | Voltage_Bus_P_Half | U16 | 0.1 | V |  |  | R | BUS正半电压 | BUS positive half voltage | Installers
|  | 06D2 | Voltage_Bus_N_Half | U16 | 0.1 | V |  |  | R | BUS负半电压 | BUS negative half voltage | Installers
飞跨电容电压 | Fly across capacitor voltage | 06D3 -- 06E2 | FlyingCap_Voltage1 -- 16 | U16 | 0.1 | V |  |  | R | PV1-16飞跨电容电压（16个） | PV1-16 Fly Across Capacitor Voltages (16) | Installers
内部信息 | Internal information | 06E3 -- 06EC | Internal_Info1 -- 10 | U16 | 0.1 | V |  |  | R | 内部信息1-10（10个，调试信息区） | Internal messages 1-10 (10, commissioning message area) | Installers
逆变器额定功率 | Inverter power rating | 06ED | RatedPower_Inverter | U16 | 0.1kW | kW |  |  | R | 逆变器额定功率 | Inverter power rating
IV曲线扫描 | IV curve scan | 06EE | IVPoints_Effec_Num | U16 | 1 |  | 1 | 150 | R | IV曲线扫描有效点的个数 | Number of valid points for IV curve scan
2.8Confluence information(0x0700-0x077F)
|  | 0700 -- 0703 | AddressMask_Realtime_CombinerInfo1 | U64 |  |  |  |  | R | 本地址开始的64个寄存器地址字的掩码区。 参看地址0x0040的说明 | Mask area for the 64 register address words starting at this address. Refer to the description of address 0x0040 | Installers | 00000000 | 0000000F
第1-16组 汇流电压 组串电流 | Group 1 - 16 Convergence voltage String current | 0704 -- 0731 | Voltage_Group1 -- 16 | U16 | 0.1 | V |  |  | R | 第1-16组汇流电压（16个）。 | Group 1-16 sink voltages (16). | [7 empty] | 与PV1电压相等，地址从0x0704开始，每组间隔3个地址。例：0x0866表示215V | Equal to PV1 voltage, addresses start at 0x0704, each group is spaced 3 addresses apart. Example: 0x0866 means 215V
|  | 0705 -- 0732 | Current_Group1_Branch1 -- Current_Group16_Branch1 | U16 | 0.01 | A |  |  | R | 第1-16组第1路组串电流（16个）。 | Group 1-16 1st group string currents (16) | [7 empty] | 与PV1电流相等，地址从0x0705开始，每组间隔3个地址，注意还有第3-4路组串电流，地址从0x0744开始。 例：0x015F表示3.51A | Equal to PV1 current, address from 0x0705, 3 addresses per group interval, note that there is also a 3rd-4th group string current, address from 0x0744. Example: 0x015F means 3.51A
|  | 0706 -- 0733 | Current_Group1_Branch2 -- Current_Group16_Branch2 | U16 | 0.01 | A |  |  | R | 第1-16组第2路组串电流（16个）。 | Group 1-16 2nd string currents (16) | [7 empty] | 是否具备此功能与机型相关，案例参考第1组第1路组串电流，地址从0x0706开始，每组间隔3个地址，注意还有第3-4路组串电流，地址从0x0744开始。 | Availability of this function is model dependent, case reference group 1 1st string current, address starting at 0x0706, each group is spaced 3 addresses apart, note there is also a 3rd-4th string current, address starting at 0x0744.
|  | 0734 -- 073F | [7 empty] | 预留 | Reserved
|  | 0740 -- 0743 | AddressMask_Realtime_CombinerInfo2 | U64 |  |  |  |  | R | 本地址开始的64个寄存器地址字的掩码区。 参看地址0x0040的说明 | Mask area for the 64 register address words starting at this address. Refer to description of address 0x0040 | Installers | 00000000 | 0000000F
第1-16组 汇流 组串电流 | Group 1-16 Sink current String current | 0744 -- 0762 | Current_Group1_Branch3 -- Current_Group16_Branch3 | U16 | 0.01 | A |  |  | R | 第1-16组第3路组串电流（16个）。 | Group 1-16 3rd way group string current (16) | [7 empty] | 是否具备此功能与机型相关 案例参考第1组第1路组串电流 每组间隔2个地址。 | Availability of this function is model dependent Case reference group 1 1st string current Each group is spaced at 2 addresses.
|  | 0745 -- 0763 | Current_Group1_Branch4 -- Current_Group16_Branch4 | U16 | 0.01 | A |  |  | R | 第1-16组第4路组串电流（16个）。 | Group 1-16 4th way string current (16)
|  | 0764 -- 077F | [7 empty] | 预留 | Reserved
2.9 Pull arc information (0x0780-0x07C8) The function of this block address is not used yet
|  | 0780 -- 0783 | AddressMask_Realtime_ArcInfo3 | U64 |  |  |  |  | R | 本地址开始的64个寄存器地址字的掩码区。 参看地址0x0040的说明 | Mask area for the 64 register address words starting at this address. Refer to the description of address 0x0040 | Installers | 00000000 | 0000000F
实时电弧强度 | Real-time arc intensity | 0784 -- 079B | ArcStrength_MPPT_1 -- 24 | I16 | 1 |  |  |  | R | MPPT 1 - 24 监测的实时电弧强度（24个） | MPPT 1 - 24 Real-time arc intensity monitored (24)
|  | 079C -- 07A1 | [7 empty] | 预留 | Reserved
电弧强度历史值 | Arc intensity history | 07A2 -- 07B9 | ArcStrength_history_Channel1 -- 24 | I16 | 1 |  |  |  | R | 通道 1 -24 上电后记录监测到的电弧强度历史最大值，掉电后自动清除（24个） | Channels 1 - 24 Historical maximum value of monitored arc intensity recorded after power-up and automatically cleared after power-down (24)
|  | 07BA -- 07BF | [7 empty] | 预留 | Reserved
|  | 07C0 -- 07C3 | AddressMask_Realtime_ArcInfo4 | U64 |  |  |  |  | R | 本地址开始的64个寄存器地址字的掩码区。 参看地址0x0040的说明 | Mask area for 64 register address words starting at this address. Refer to description of address 0x0040 | Installers | 00000000 | 0000000F
电弧极值 | Arc polarity values | 07C4 | arc_peak_to_peak | U16 | 1 |  |  |  | R | 电弧最大峰峰值 | Maximum peak-to-peak value of the arc
|  | 07C5 | arc_variance | U16 | 1 |  |  |  | R | 电弧最大方差 | Arc maximum variance
|  | 07C6 | arc_harmonic_energy | U16 | 1 |  |  |  | R | 电弧最大谐波能量 | Arc maximum harmonic energy
|  | 07C7 | arc_amplitude_variance | U16 | 1 |  |  |  | R | 电弧最大幅值方差 | Arc maximum amplitude variance
三、Safety parameters area(0x0800-0x0FFF)
3.1Start-up parameters(0x0800-0x083F)
|  | 0800 | ConnectWaitTime | U16 | 1 | 秒 | 1 | 65535 | RW | 并网前等待时间 | Waiting time before grid connection | Installers | [6 empty] | 此界面寄存器都是互相独立的设定参数功能 | The interface registers are all independent of each other for setting parameter functions
|  | 0801 | PowerUpSpeed | U16 | 1 | %Pn/min | 1 | 3000 | RW | 100表示1分钟升到满载对应的速率，其他值以此为基准进行乘除计算 注：并网上升速度 | 100 indicates the rate corresponding to a 1-minute rise to full load, other values are multiplied and divided on this basis Note: Grid connection rise rate | Installers
|  | 0802 | ReconnectWaitTime | U16 | 1 | 秒 | 1 | 65535 | RW | 电网故障恢复后重新并网前等待时间 | Waiting time before re-connecting to the grid after grid failure recovery | Installers
|  | 0803 | ReconnectPowerUpSpeed | U16 | 1 | %Pn/min | 1 | 3000 | RW | 100表示1分钟升到满载对应的速率，其他值以此为基准进行乘除计算 注：电网故障恢复后上升速度 | 100 indicates the rate at which 1 minute rises to full load, other values are multiplied and divided by this. | Installers
|  | 0804 | VoltHighLimit | U16 | 0.1 | V | 0 | 65535 | RW | 启动电网电压上限 注：电网启动时的电压不能超过此设定值 | Upper limit of grid start-up voltage Note: The grid start-up voltage must not exceed this setting | End-users
|  | 0805 | VoltLowLimit | U16 | 0.1 | V | 0 | 65535 | RW | 启动电网电压下限 注：电网启动时的电压不能低于此设定值 | Lower limit of the start-up grid voltage Note: The voltage at start-up cannot be lower than this setting | End-users
|  | 0806 | FreqHighLimit | U16 | 0.01 | Hz | 4000 | 7000 | RW | 启动电网频率上限 | Start grid frequency upper limit | End-users
|  | 0807 | FreqLowLimit | U16 | 0.01 | Hz | 4000 | 7000 | RW | 启动电网频率下限 | Lower limit of start-up grid frequency | End-users
|  | 0808 | ReconnectVoltHighLimit | U16 | 0.1 | V | 0 | 65535 | RW | 重连电网电压上限 | Reconnect grid voltage upper limit | End-users
|  | 0809 | ReconnectVoltLowLimit | U16 | 0.1 | V | 0 | 65535 | RW | 重连电网电压下限 | Lower limit of reconnected grid voltage | End-users
|  | 080A | ReconnectFreqHighLimit | U16 | 0.01 | Hz | 4000 | 7000 | RW | 重连电网频率上限 注：重连启动时的电压频率不能超过此设定值 | Upper limit of reconnect grid frequency Note: The voltage and frequency at reconnect start cannot exceed this setting | End-users
|  | 080B | ReconnectFreqLowLimit | U16 | 0.01 | Hz | 4000 | 7000 | RW | 重连电网频率下限 注：重连启动时的电压频率不能低于此设定值 | Lower limit of reconnection grid frequency Note: The voltage and frequency at reconnection start cannot be lower than this setting | End-users
3.2Voltage protection parameters(0x0840-0x087F)
|  | 0840 | Voltage Config | U16 |  |  |  |  | RW | Bit0：过压一级保护使能位 Bit1：过压二级保护使能位 Bit2：过压三级保护使能位 Bit3：欠压一级保护使能位 Bit4：欠压二级保护使能位 Bit5：欠压三级保护使能位 Bit6：10分钟过压保护使能位 注：使能为置1为开，置0为关 | Bit0: Overvoltage primary protection enable bit Bit1: Overvoltage secondary protection enable bit Bit2: Overvoltage level 3 protection enable bit Bit3: Undervoltage primary protection enable bit Bit4: Undervoltage secondary protection enable bit Bit5: Undervoltage level 3 protection enable bit Bit6: 10 minutes overvoltage protection enable bit Note: Enable is set to 1 for on, set to 0 for off | Installers | [6 empty] | 过压一/二/三级保护使能位分别控制着一/二/三级过压保护值和一/二/三级过压保护时间。 欠压一/二/三级保护使能位分别控制着一/二/三级欠压保护值和一/二/三级欠压保护时间。10分钟过压保护使能位控制着电网10分钟过压保护值。 只有使能位打开，对应寄存器的功能才能体现。 | The overvoltage 1, 2 and 3 protection enable bits control the overvoltage protection values and the overvoltage protection times of 1, 2 and 3, respectively. The 10-minute overvoltage protection enable bit controls the 10-minute overvoltage protection value of the grid. Only when the enable bit is turned on, the function of the corresponding register can be reflected.
|  | 0841 | RatedVoltage | U16 | 0.1 | V | 0 | 65535 | RW | 额定电网电压 | Rated grid voltage | Installers
|  | 0842 | FirstOvervoltageProtectionValue | U16 | 0.1 | V | 0 | 65535 | RW | 一级过压保护值 注：设定的第一级电压保护阈值，超过触发保护机制 | Note: The first level of voltage protection threshold is set and exceeds the trigger protection mechanism | End-users
|  | 0843 | FirstOvervoltageProtectionTime | U16 | 10 | ms | 1 | 65535 | RW | 一级过压保护时间 注：设定的第一级电压时间阈值，超过触发保护机制 | First-level overvoltage protection time Note: Set threshold for first-level voltage time, exceeds trigger protection mechanism | Installers
|  | 0844 | SecondOvervoltageProtectionValue | U16 | 0.1 | V | 0 | 65535 | RW | 二级过压保护值 | Secondary overvoltage protection value | End-users
|  | 0845 | SecondOvervoltageProtectionTime | U16 | 10 | ms | 1 | 65535 | RW | 二级过压保护时间 | Secondary overvoltage protection time | Installers
|  | 0846 | ThirdOvervoltageProtectionValue | U16 | 0.1 | V | 0 | 65535 | RW | 三级过压保护值 | Tertiary overvoltage protection value | End-users
|  | 0847 | ThirdOvervoltageProtectionTime | U16 | 10 | ms | 1 | 65535 | RW | 三级过压保护时间 | Three-stage overvoltage protection time | Installers
|  | 0848 | FirstUnderVoltageProtectionValue | U16 | 0.1 | V | 0 | 65535 | RW | 一级欠压保护值 | Level 1 undervoltage protection value | End-users
|  | 0849 | FirstUndervoltageProtectionTime | U16 | 10 | ms | 1 | 65535 | RW | 一级欠压保护时间 | Primary undervoltage protection time | Installers
|  | 084A | SecondUnderVoltageProtectionValue | U16 | 0.1 | V | 0 | 65535 | RW | 二级欠压保护值 | Secondary undervoltage protection value | End-users
|  | 084B | SecondUndervoltageProtectionTime | U16 | 10 | ms | 1 | 65535 | RW | 二级欠压保护时间 | Secondary undervoltage protection time | Installers
|  | 084C | ThirdUnderVoltageProtectionValue | U16 | 0.1 | V | 0 | 65535 | RW | 三级欠压保护值 | Three-stage undervoltage protection value | End-users
|  | 084D | ThirdUndervoltageProtectionTime | U16 | 10 | ms | 1 | 65535 | RW | 三级欠压保护时间 | Three-level undervoltage protection time | Installers
|  | 084E | 10MinOvervoltageProtectionValue | U16 | 0.1 | V | 0 | 65535 | RW | 电网10分钟过压保护值 | Grid 10-minute overvoltage protection value | Installers
|  | 084F | FirstOvervoltageProtectionTimeHi | U16 |  |  | 0 | 255 | RW | 一级过压保护时间高位 | Primary overvoltage protection time high | Installers | [6 empty] | 注：该寄存器与一级过压保护时间组合成32位寄存器使用 | Note: This register is used in combination with the primary overvoltage protection time to form a 32-bit register
|  | 0850 | SecondOvervoltageProtectionTimeHi | U16 |  |  | 0 | 255 | RW | 二级过压保护时间高位 | Secondary overvoltage protection time high | Installers | [6 empty] | 注：该寄存器与二级过压保护时间组合成32位寄存器使用 | Note: This register is used in combination with the secondary overvoltage protection time to form a 32-bit register
|  | 0851 | ThirdOvervoltageProtectionTimeHi | U16 |  |  | 0 | 255 | RW | 三级过压保护时间高位 | Three-level overvoltage protection time high | Installers | [6 empty] | 注：该寄存器与三级过压保护时间组合成32位寄存器使用 | Note: This register is used in combination with the three-stage overvoltage protection time to form a 32-bit register
3.3Frequency protection parameters(0x0880-0x08BF)
|  | 0880 | FrequencyConfig | U16 |  |  |  |  | RW | Bit0 过频一级保护使能位 Bit1 过频二级保护使能位 Bit2 过频三级保护使能位 Bit3 欠频一级保护使能位 Bit4 欠频二级保护使能位 Bit5 欠频三级保护使能位 注：使能为置1为开，置0为关 | Bit0 Overfrequency primary protection enable bit Bit1 Overfrequency secondary protection enable bit Bit2 Overfrequency level 3 protection enable bit Bit3 Underfrequency primary protection enable bit Bit4 Underfrequency secondary protection enable bit Bit5 Underfrequency level 3 protection enable bit Note: Enable is set to 1 for on, set to 0 for off | Installers | [6 empty] | 过频一/二/三级保护使能位分别控制着一/二/三级过频保护值和一/二/三过频保护时间。 欠频一/二/三级保护使能位分别控制着一/二/三级欠频保护值和一/二/三欠频保护时间。 只有使能位打开，对应寄存器的功能才能体现。 | The Overfrequency I/II/III protection enable bits control the I/II/III overfrequency protection value and I/II/III overfrequency protection time respectively. The underfrequency 1, 2 and 3 protection enable bits control the 1, 2 and 3 underfrequency protection values and the 1, 2 and 3 underfrequency protection times respectively. Only when the enable bit is turned on can the function of the corresponding register be reflected.
|  | 0881 | RatedFrequency | U16 | 0.01 | Hz | 4000 | 7000 | RW | 额定电网频率 | Rated grid frequency | Installers
|  | 0882 | FirstOverfrequencyProtectionValue | U16 | 0.01 | Hz | 4000 | 7000 | RW | 一级过频保护值 注：一级频率保护阈值，超过触发保护机制 | Primary overfrequency protection value Note: Primary frequency protection threshold, exceeds trigger protection mechanism | End-users
|  | 0883 | FirstOverfrequencyProtectionTime | U16 | 10 | ms | 1 | 65535 | RW | 一级过频保护时间 注：一级频率时间保护阈值，超过触发保护机制 | Primary overfrequency protection time Note: Primary frequency time protection threshold, exceeds the trigger protection mechanism | Installers
|  | 0884 | SecondOverfrequencyProtectionValue | U16 | 0.01 | Hz | 4000 | 7000 | RW | 二级过频保护值 | Secondary overfrequency protection value | End-users
|  | 0885 | SecondOverfrequencyProtectionTime | U16 | 10 | ms | 1 | 65535 | RW | 二级过频保护时间 | Secondary overfrequency protection time | Installers
|  | 0886 | ThirdOverfrequencyProtectionValue | U16 | 0.01 | Hz | 4000 | 7000 | RW | 三级过频保护值 | Level 3 overfrequency protection value | End-users
|  | 0887 | ThirdOverfrequencyProtectionTime | U16 | 10 | ms | 1 | 65535 | RW | 三级过频保护时间 | Level 3 overfrequency protection time | Installers
|  | 0888 | FirstUnderfrequencyProtectionValue | U16 | 0.01 | Hz | 4000 | 7000 | RW | 一级欠频保护值 | Level 1 under-frequency protection value | End-users
|  | 0889 | FirstUnderfrequencyProtectionTime | U16 | 10 | ms | 1 | 65535 | RW | 一级欠频保护时间 | Level 1 underfrequency protection time | Installers
|  | 088A | SecondUnderfrequencyProtectionValue | U16 | 0.01 | Hz | 4000 | 7000 | RW | 二级欠频保护值 | Secondary underfrequency protection value | End-users
|  | 088B | SecondUnderfrequencyProtectionTime | U16 | 10 | ms | 1 | 65535 | RW | 二级欠频保护时间 | Secondary underfrequency protection time | Installers
|  | 088C | ThirdUnderfrequencyProtectionValue | U16 | 0.01 | Hz | 4000 | 7000 | RW | 三级欠频保护值 | Three-level under-frequency protection value | End-users
|  | 088D | ThirdUnderfrequencyProtectionTime | U16 | 10 | ms | 1 | 65535 | RW | 三级欠频保护时间 | Three-level under-frequency protection time | Installers
|  | 088E | FirstOverfrequencyProtectionTimeHi | U16 |  |  | 0 | 255 | RW | 一级过频保护时间高位 | Level 1 overfrequency protection time high | [7 empty] | 注：该寄存器与一级过频保护时间组合成32位寄存器使用 | Note: This register is used in combination with the primary overclock protection time to form a 32-bit register
|  | 088F | SecondOverfrequencyProtectionTimeHi | U16 |  |  | 0 | 255 | RW | 二级过频保护时间高位 | Secondary overfrequency protection time high | [7 empty] | 注：该寄存器与二级过频保护时间组合成32位寄存器使用 | Note: This register is used in combination with the secondary overclock protection time to form a 32-bit register
|  | 0890 | ThirdOverfrequencyProtectionTimeHi | U16 |  |  | 0 | 255 | RW | 三级过频保护时间高位 | Three-level underfrequency protection time high | [7 empty] | 注：该寄存器与三级过频保护时间组合成32位寄存器使用 | Note: This register is used in combination with the Level 3 under-frequency protection time to form a 32-bit register
|  | 0891 | FirstUnderfrequencyProtectionTimeHi | U16 |  |  | 0 | 255 | RW | 一级欠频保护时间高位 | Level 1 underfrequency protection time high | [7 empty] | 注：该寄存器与一级欠频保护时间组合成32位寄存器使用 | Note: This register is used in combination with the primary under frequency protection time to form a 32-bit register.
|  | 0892 | SecondUnderfrequencyProtectionTimeHi | U16 |  |  | 0 | 255 | RW | 二级欠频保护时间高位 | Secondary underfrequency protection time high | [7 empty] | 注：该寄存器与二级欠频保护时间组合成32位寄存器使用 | Note: This register is used in combination with the secondary underfrequency protection time to form a 32-bit register
|  | 0893 | ThirdUnderfrequencyProtectionTimeHi | U16 |  |  | 0 | 255 | RW | 三级欠频保护时间高位 | Level 3 underfrequency protection time high | [7 empty] | 注：该寄存器与三级欠频保护时间组合成32位寄存器使用 | Note: This register is used in combination with the Level 3 under-frequency protection time to form a 32-bit register
3.4DCI protection parameters(0x08C0-0x08FF)
|  | 08C0 | DCI Config | U16 |  |  |  |  | RW | Bit0：DCI 一级保护使能位 Bit1：DCI 二级保护使能位 Bit2：DCI 三级保护使能位 Bit3：DCI 测试使能位 注：使能为置1为开，置0为关 | Bit0: DCI primary protection enable bit Bit1: DCI secondary protection enable bit Bit2: DCI tertiary protection enable bit Bit3: DCI test enable bit Note: enable is set to 1 for on, set to 0 for off | Installers | [6 empty] | DCI 一/二/三级保护使能位分别控制着DCI一/二/三级保护值和DCI一/二/三级保护时间。 DCI测试使能位控制着DCI （R、S、T）三相测试值只有使能位打开，对应寄存器的功能才能体现。 | The DCI 1st/2nd/3rd protection enable bits control the DCI 1st/2nd/3rd protection value and the DCI 1st/2nd/3rd protection time, respectively. The DCI test enable bit controls the DCI (R, S, T) three-phase test value Only when the enable bit is turned on, the function of the corresponding register can be reflected.
|  | 08C1 | DCIFirstProtectionValue | U16 | 1 | mA | 1 | 65535 | RW | DCI一级保护值 | DCI primary protection value | Installers | [6 empty] | 注：直流分量一级保护阈值，超过触发保护机制 | Note: DC component level 1 protection threshold, exceeds trigger protection mechanism
|  | 08C2 | DCIFirstProtectionTime | U16 | 10 | ms | 1 | 65535 | RW | DCI一级保护时间 | DCI primary protection time | Installers | [6 empty] | 注：直流分量一级时间保护阈值，超过触发保护机制 | Note: DC component level 1 time protection threshold, exceeding the trigger protection mechanism
|  | 08C3 | DCISecondProtectionValue | U16 | 1 | mA | 1 | 65535 | RW | DCI二级保护值 | DCI secondary protection value | Installers
|  | 08C4 | DCISecondProtectionTime | U16 | 10 | ms | 1 | 65535 | RW | DCI二级保护时间 | DCI secondary protection time | Installers
|  | 08C5 | DCIThirdProtectionValue | U16 | 1 | mA | 1 | 65535 | RW | DCI三级保护值 | DCI tertiary protection value | Installers
|  | 08C6 | DCIThirdProtectionTime | U16 | 10 | ms | 1 | 65535 | RW | DCI三级保护时间 | DCI tertiary protection time | Installers
|  | 08C7 | DCITestValue1 | I16 | 1 | mA | -32768 | 32767 | RW | DCI R相测试值 | DCI R-phase test value | Installers | [6 empty] | 注：直流分量R相测试设定值 | Note: DC component R-phase test setpoint
|  | 08C8 | DCITestValue2 | I16 | 1 | mA | -32768 | 32767 | RW | DCI S相测试值 | DCI S-phase test value | Installers
|  | 08C9 | DCITestValue3 | I16 | 1 | mA | -32768 | 32767 | RW | DCI T相测试值 | DCI T-phase test value | Installers
|  | 08CA | DCIFirstProtectionProportion | U16 | 0.01 | % | 1 | 65535 | RW | DCI一级保护比例 | DCI primary protection ratio | Installers | [6 empty] | 注：直流分量一级保护比例 | Note: DC component level 1 protection ratio
|  | 08CB | DCISecondProtectionProportion | U16 | 0.01 | % | 1 | 65535 | RW | DCI二级保护比例 | DCI secondary protection ratio | Installers
|  | 08CC | DCIThirdProtectionProportion | U16 | 0.01 | % | 1 | 65535 | RW | DCI三级保护比例 | DCI tertiary protection ratio | Installers
3.5Active, over- and under-voltage load shedding parameters(0x0900-0x093F)
|  | 0900 | Remote Config | U16 |  |  |  |  | RW | Bit0：有功降载使能位 Bit1：远程开关机使能位 Bit2：过压降载使能位 Bit3：过压充电降载使能位 Bit4：欠压降充电功率使能位 Bit5：DRM0使能位 Bit6：逻辑接口（DRM1-8）使能位 Bit7：防逆流过载使能位 Bit8：电压降载PT曲线使能位 Bit9：远程关机降载使能位(0：默认直接关机，1：斜率降载关机) 注：使能为置1为开，置0为关 | Bit0: Active down load enable bit Bit1: Remote switch-on/off enable bit Bit2: overvoltage down load enable bit Bit3: overvoltage charge down enable bit Bit4: Under-voltage charge-down power enable bit Bit5: DRM0 enable bit Bit6: Logic interface (DRM1-8) enable bit Bit7: Anti-backflow overload enable bit Bit8: Voltage drop-down PT curve enable bit Bit9: Remote shutdown down load enable bit (0: default direct shutdown, 1: ramp down load shutdown) Note: Enable is set to 1 for on, set to 0 for off | Installers | [6 empty] | 有功降载使能位控制有功输出百分比和有功降载速率 远程开关机使能位控制远程开关机。 过压降载使能位控制电网过压降载起始点/终止点/截止功率和过压降载速率。 欠压降充电功率使能位控制着电网欠压降载起始点/终止点/截止功率。 电压降载PT曲线使能位控制着电压降载时间。 逻辑接口使能位控制着逻辑接口（1-8）对应功率。 防逆流过载使能位控制着防逆流功率、防逆流过载时间、逻辑接口降载速率、逻辑接口回载速率。 只有使能位打开，对应寄存器的功能才能体现。 | The active load shedding enable bit controls the active output percentage and active load shedding rate The remote switch-on enable bit controls remote switch-off. The overvoltage derate enable bit controls the grid overvoltage derate start/end/cut-off power and the overvoltage derate rate. The undervoltage step-down power enable bit controls the grid undervoltage step-down start/end/cut-off power. The voltage step-down PT curve enable bit controls the voltage step-down time. The logic interface enable bit controls the power corresponding to the logic interface (1-8). The anti-backflow overload enable bit controls the anti-backflow power, the anti-backflow overload time, the logical interface down load rate and the logical interface back load rate. Only when the enable bit is turned on can the function of the corresponding register be reflected.
|  | 0901 | ActiveOutputLimit | U16 | 0.1 | % | 0 | 1000 | RW | 有功输出百分比 | Active output percentage | Installers
|  | 0902 | ActiveOutputDownSpeed | U16 | 1 | %Pn/min | 1 | 300 | RW | 有功降载速率 | Active load shedding rate
|  | 0903 | GridVoltageDropStart | U16 | 0.1 | V | 0 | 65535 | RW | 电网过压降载起始点 | Grid overvoltage load shedding start point | Installers
|  | 0904 | GridVoltageDropStop | U16 | 0.1 | V | 0 | 65535 | RW | 电网过压降载终止点 | Grid overvoltage derate cut-off point | Installers
|  | 0905 | GridVoltageDropMinPower | I16 | 1 | % | -100 | 100 | RW | 电网过压降载截止功率 | Grid over-voltage derating cut-off power | Installers
|  | 0906 | OvervoltageDownSpeed | U16 | 1 | %Pn/min | 1 | 300 | RW | 过压降载速率 | Over-voltage derating rate | Installers
|  | 0907 | ChgDerateVoltStart | U16 | 0.1 | V | 0 | 65535 | RW | 电网欠压降载起始点 | Grid under-voltage load shedding start point | Installers
|  | 0908 | ChgDerateVoltEnd | U16 | 0.1 | V | 0 | 65535 | RW | 电网欠压降载终止点 | Grid undervoltage cut-off point | Installers
|  | 0909 | ChgDerateMinPower | I16 | 1 | % | -100 | 100 | RW | 电网欠压降载截止功率 | Grid undervoltage cut-off power | Installers
|  | 090A -- 0911 | PowerForLogic1 -- 8 | I16 | 1 | % | -100 | 100 | RW | 逻辑接口1-8对应功率（8个） | Power corresponding to logic interfaces 1-8 (8) | Installers
|  | 0912 | RefluxPower | U16 | 1 | % | 0 | 100 | RW | 防逆流功率（VDE4105安规并网功率上限） | Anti-backflow power (VDE4105 safety regulation grid-connected power limit) | Installers
|  | 0913 | RefluxOVloadTime | U16 | 10 | ms | 0 | 65535 | RW | 防逆流过载时间（VDE4105安规逆流过载脱网时间） | Anti-backflow overload time (VDE4105 safety regulation backflow overload off-grid time) | Installers
|  | 0914 | LogicDerateSpeed | U16 | 1 | %Pn/min | 1 | 65535 | RW | 逻辑接口降载速率 | Logical interface down load rate | Installers
|  | 0915 | LogicReloadSpeed | U16 | 1 | %Pn/min | 1 | 65535 | RW | 逻辑接口回载速率 | Logical interface return load rate | Installers
|  | 0916 | VoltageDerateResponseTime | U16 | 1 | 秒 | 0 | 65535 | RW | 电压降载时间 | Voltage down load rate | Installers
|  | 0917 | PowerDownSpeed | U16 | 1 | %Pn/min | 1 | 3000 | RW | 远程关机降载速率 | Remote shutdown down rate | Installers
3.6Over-under frequency derating parameters(0x0940-0x097F)
|  | 0940 | FrequencyDerateConfig | U16 |  |  |  |  | RW | Bit0：过频输出降载使能 Bit1：欠频输入降载使能 Bit2：过频回载使能 Bit3：欠频回载使能 Bit4：过频从额定功率开始降载使能 Bit5：当前功率计算降载斜率使能 Bit6：储能分段曲线使能 Bit7：最大功率计算使能 Bit8: 欠频从额定功率开始降载使能 Bit12-13：降载模式（0斜率模式/1频率范围模式） 注：225kw光伏机型不支持储能分段曲线使能和最大功率计算使能功能。 注：225kw机型从额定功率开始降载使能和当前功率计算降载斜率使能此界面未能体现 注：此参数界面区分为了光伏和储能两大界面注：使能为置1为开，置0为关 | Bit0: Overclocked output down load enable Bit1: Underclocked input down load enable Bit2: Overclock back enable Bit3: Underfrequency return enable Bit4: Overfrequency down load enable from rated power Bit5: Current power calculation ramp down enable Bit6: Energy storage segmentation curve enable Bit7: Maximum power calculation enable Bit8: Underfrequency download from rated power enable Bit12-13: Load down mode (0 slope mode/1 frequency range mode) Note: 225kw PV models do not support the energy storage segmentation curve enable and maximum power calculation enable functions. Note: The 225kw model does not support the load shedding enable from the rated power and the current power calculation load shedding ramp enable in this interface Note: This parameter interface area is divided into two interfaces, PV and energy storage Note: Enable is set to 1 for on, set to 0 for off | Installers | [6 empty] | 过频输出降载使能控制着降载模式（0斜率模式/1频率范围模式），0斜率模式控制着过频降载（起始频率/斜率百分比/启动等待时间），1频率范围模式控制着过频降载（起始频率/截止频率/启动等待时间）。 欠频输入降载使能控制着欠频降载起始频率/截止频率/斜率百分比/启动等待时间。 过频回载使能控制着过频回载等待时间/过频降载回载频率/过频回载截速率百分比。 欠频回载使能控制着欠频回载等待时间/欠频降载回载频率/欠频回载截速率百分比和退出降载最高/低频率只有使能位打开，对应寄存器的功能才能体现。 | The overfrequency output down load enable controls the down load mode (0 slope mode/1 frequency range mode), the 0 slope mode controls the overfrequency down load (start frequency/slope percentage/start wait time) and the 1 frequency range mode controls the overfrequency down load (start frequency/cutoff frequency/start wait time). The underfrequency input load-down enable controls the underfrequency load-down start frequency/cut-off frequency/slope percentage/start-up wait time. The overfrequency return enable controls the overfrequency return wait time/overfrequency dropback frequency/overfrequency return cut-off rate percentage. The underfrequency return enable controls the underfrequency return wait time/underfrequency down load return frequency/underfrequency return cut-off rate percentage and the exit dropout maximum/low frequency only if the enable bit is turned on, the function of the corresponding register can be reflected.
|  | 0941 | OverfrequencyStart | U16 | 0.01 | Hz | 4000 | 7000 | RW | 过频降载起始频率 | Overfrequency load shedding starting frequency | Installers
|  | 0942 | OverfrequencyEnd | U16 | 0.01 | Hz | 4000 | 7000 | RW | 过频降载截止频率。频率范围模式有效 | Over-frequency load shedding cut-off frequency. Valid in frequency range mode | Installers
|  | 0943 | OverfrequencySlope | U16 | 1 | %Pn/Hz | 1 | 300 | RW | 过频降载斜率百分比。斜率模式有效 德标slope=1/(s*fn) | Overfrequency ramp down percentage. Slope mode valid DeMarker slope=1/(s*fn) | Installers
|  | 0944 | OverfrequencyResponseDelay | U16 | 10 | ms | 0 | 65535 | RW | 过频降载启动等待时间 | Overfrequency download start wait time | Installers
|  | 0945 | OverfrequencyReloadDelay | U16 | 10 | ms | 0 | 65535 | RW | 过频回载前等待时间 | Waiting time before overfrequency loadback | Installers
|  | 0946 | OverfrequencyReloadStart | U16 | 0.01 | Hz | 4000 | 7000 | RW | 过频降载回载频率。禁止过频回载时生效。 | Overfrequency down load return frequency. Effective when overfrequency reload is disabled. | Installers
|  | 0947 | OverfrequencyReloadSpeed | U16 | 1 | %Pn/min | 1 | 300 | RW | 过频回载速率百分比 | Percentage of overfrequency reload rate | Installers
|  | 0948 | UnderfrequencyStart | U16 | 0.01 | Hz | 4000 | 7000 | RW | 欠频降载起始频率 | Under frequency down load start frequency | Installers
|  | 0949 | UnderfrequencyEnd | U16 | 0.01 | Hz | 4000 | 7000 | RW | 欠频降载截止频率。频率范围模式有效 | Underclocking cut-off frequency. Valid for frequency range mode | Installers
|  | 094A | UnderfrequencySlope | U16 | 1 | %Pn/Hz | 1 | 300 | RW | 欠频降载斜率百分比。斜率模式有效 | Underfrequency derate slope percentage. Ramp mode is valid | Installers
|  | 094B | UnderfrequencyResponseDelay | U16 | 10 | ms | 0 | 65535 | RW | 欠频降载启动等待时间 | Undervoltage download start wait time | Installers
|  | 094C | UnderfrequencyReloadDelay | U16 | 10 | ms | 0 | 65535 | RW | 欠频回载前等待时间 | Waiting time before underload. | Installers
|  | 094D | UnderfrequencyReloadStart | U16 | 0.01 | Hz | 4000 | 7000 | RW | 欠频降载回载频率。禁止欠频回载时生效。 | Under frequency down load return frequency. Effective when under-frequency reload is disabled. | Installers
|  | 094E | UnderfrequencyReloadSpeed | U16 | 1 | %Pn/min | 1 | 300 | RW | 欠频回载速率百分比 | Underfrequency reload rate percentage | Installers
|  | 094F | FrequencyRecoverMax | U16 | 0.01 | Hz | 4000 | 7000 | RW | 退出降载最高频率。过欠频共用。允许过频回载时生效 | Maximum frequency to exit the underload. Over-under frequency sharing. Effective when overfrequency loadback is allowed | Installers
|  | 0950 | FrequencyRecoverMin | U16 | 0.01 | Hz | 4000 | 7000 | RW | 退出降载最低频率。过欠频共用。允许欠频回载时生效 | Exits the lowest frequency of the dropout. Shared over-under frequency. Effective when underload is allowed | Installers
|  | 0951 | ESSOverFrequencyStart | U16 | 0.01 | Hz | 4000 | 7000 | RW | （储能）过频降载起始频率 | (Energy storage) Overload start frequency | Installers
|  | 0952 | ESSOverfrequencyEnd | U16 | 0.01 | Hz | 4000 | 7000 | RW | （储能）过频降载截止频率。频率范围模式有效 | (Energy storage) Overdrive cut-off frequency. Valid in frequency range mode
|  | 0953 | ESSOverFrequencySlope | U16 | 1 | %Pn/Hz | 1 | 300 | RW | （储能）过频降载斜率百分比。斜率模式有效 德标slope=1/(s*fn) | (Energy Storage) Overfrequency Derate Ramp Percentage. Slope mode valid German Standard slope=1/(s*fn) | Installers
|  | 0954 | ESSOverFrequencyResponseDelay | U16 | 10 | ms | 0 | 65535 | RW | （储能）过频降载启动等待时间 | (Energy storage) Overfrequency download start-up waiting time | Installers
|  | 0955 | ESSOverFrequencyReloadDelay | U16 | 10 | ms | 0 | 65535 | RW | （储能）过频回载前等待时间 | (Energy storage) Waiting time before overfrequency return to load | Installers
|  | 0956 | ESSOverfrequencyReloadStart | U16 | 0.01 | Hz | 4000 | 7000 | RW | （储能）过频降载回载频率。禁止过频回载时生效。 | (energy storage) Overfrequency down load return frequency. Effective when overfrequency backload is disabled. | Installers
|  | 0957 | ESSOverFrequencyReloadSpeed | U16 | 1 | %Pn/min | 1 | 300 | RW | （储能）过频回载速率百分比 | (Energy storage) Percentage of overload rate | Installers
|  | 0958 | ESSUnderFrequencyStart | U16 | 0.01 | Hz | 4000 | 7000 | RW | （储能）欠频降载起始频率 | (Energy storage) Underfrequency down load start frequency | Installers
|  | 0959 | ESSUnderfrequencyEnd | U16 | 0.01 | Hz | 4000 | 7000 | RW | （储能）欠频降载截止频率。频率范围模式有效 | (ENERGY STORAGE) Underfrequency derate cut-off frequency. Valid in frequency range mode
|  | 095A | ESSUnderFrequencySlope | U16 | 1 | %Pn/Hz | 1 | 300 | RW | （储能）欠频降载斜率百分比。斜率模式有效 | (Energy storage) Underfrequency derate slope percentage. Ramp mode valid | Installers
|  | 095B | ESSUnderFrequencyResponseDelay | U16 | 10 | ms | 0 | 65535 | RW | （储能）欠频降载启动等待时间 | (Energy storage) Underfrequency load shedding start wait time | Installers
|  | 095C | ESSUnderFrequencyReloadDelay | U16 | 10 | ms | 0 | 65535 | RW | （储能）欠频回载前等待时间 | (Energy storage) Waiting time before underfrequency load return | Installers
|  | 095D | ESSUnderfrequencyReloadStart | U16 | 0.01 | Hz | 4000 | 7000 | RW | （储能）欠频降载回载频率。禁止欠频回载时生效。 | (Energy storage) Underfrequency load return frequency. Effective when underfrequency reload is disabled. | Installers
|  | 095E | ESSUnderFrequencyReloadSpeed | U16 | 1 | %Pn/min | 1 | 300 | RW | （储能）欠频回载速率百分比 | (Energy storage) Underfrequency reload rate percentage | Installers
|  | 095F | ESSFrequencyRecoverMax | U16 | 0.01 | Hz | 4000 | 7000 | RW | （储能）退出降载最高频率。过欠频共用 | (Energy Storage) Maximum frequency to exit the load shedding. Over Underfrequency Common | Installers
|  | 0960 | ESSFrequencyRecoverMin | U16 | 0.01 | Hz | 4000 | 7000 | RW | （储能）退出降载最低频率。过欠频共用 | (Energy storage) Exit the lowest frequency of the load shedding. Over and under frequency sharing | Installers
|  | 0961 | ESSOverFrequencyTransition | U16 | 0.01 | Hz | 4000 | 7000 | RW | （储能）过频降载功率穿越频率点。使能0940 Bit6时有效。 | (energy storage) Overdrive power crossing frequency point. Valid when 0940 Bit6 is enabled. | Installers
|  | 0962 | ESSUnderFrequencyTransition | U16 | 0.01 | Hz | 4000 | 7000 | RW | （储能）欠频降载功率穿越频率点。使能0940 Bit6时有效。 | (energy storage) Underfrequency power down crossing frequency point. Valid when 0940 Bit6 is enabled. | Installers
3.7Reactive power parameters(0x0980-0x09BF)
|  | 0980 | ReactiveConfig | U16 |  |  |  |  | RW | Bit0：无功使能 Bit1-3：无功模式 Bit8：无功模式三电压进入使能位 Bit9：充电无功使能 Bit10：无功模式四奥地利使能位 注：无功模式bit1-3控制着六种无功模式 注：对应的无功模式下控制对应的功能，具体情况如下寄存器功能描述 注：使能为置1为开，置0为关 | Bit0: Reactive enable Bit1-3: Reactive mode Bit8: Reactive mode three-voltage entry enable bit Bit9: Charge reactive enable Bit10: Reactive mode four Austrian enable bit Note: Reactive mode bits1-3 control the six reactive modes Note: The corresponding functions are controlled in the corresponding reactive modes, as described in the following register functions Note: Enable is set to 1 for on, set to 0 for off | Installers | [6 empty] | 不同模式下控制着不同功能寄存器，每个无功模式都有一个使能位，只有对应的无功模式使能位打开才能控制其中功能寄存器。 | Different modes control different function registers. Each reactive mode has an enable bit, and only the corresponding reactive mode enable bit is turned on to control one of the function registers.
|  | 0981 | PowerFactor | I16 | 0.0001 |  | -10000 | 10000 | RW | 功率因数，用于无功模式一计算Tanphi。 正值代表提供感性欠激励无功，逆变器输出电流超前电网电压； 负值代表提供容性过激励无功，逆变器输出电流滞后电网电压； | Power factor for reactive mode one to calculate Tanphi. Positive values represent the provision of inductive under-stimulated reactive power, with the inverter output current overriding the grid voltage; A negative value means that capacitive over-excitation reactive power is provided and the inverter output current lags behind the grid voltage; | Installers
|  | 0982 | FixedReactivePercentage | I16 | 0.01 | % | -6000 | 6000 | RW | 固定无功功率百分比，用于无功模式二计算无功量。 正值代表提供感性欠激励无功，逆变器输出电流超前电网电压； 负值代表提供容性过激励无功，逆变器输出电流滞后电网电压； | Fixed reactive power percentage for reactive mode II calculation of reactive power. positive values represent the supply of inductive under-excitation reactive power and the inverter output current overruns the grid voltage; A negative value means that capacitive over-excitation reactive power is provided and the inverter output current lags behind the grid voltage; | Installers
|  | 0983 | ReactiveCos1 | I16 | 0.0001 |  | -10000 | 10000 | RW | 用于无功模式三，第一点功率因数值。 正值代表提供感性欠激励无功，逆变器输出电流超前电网电压； 负值代表提供容性过激励无功，逆变器输出电流滞后电网电压； | is used for reactive mode III, the first point power factor value. positive values represent the supply of inductive under-excitation reactive power and the inverter output current overruns the grid voltage; A negative value means that capacitive over-excitation reactive power is supplied and the inverter output current lags behind the grid voltage; | Installers
|  | 0984 | ReactivedynamicValue1 | I16 | 1 | % | -100 | 100 | RW | 用于无功模式三，第一点功率百分比 | for reactive mode III, first point power percentage | Installers
|  | 0985 | ReactiveCos2 | I16 | 0.0001 |  | -10000 | 10000 | RW | 用于无功模式三，第二点功率因数值 | for reactive mode III, second point power factor value | Installers
|  | 0986 | ReactivedynamicValue2 | I16 | 1 | % | -100 | 100 | RW | 用于无功模式三，第二点功率百分比 | for reactive mode III, second point power percentage | Installers
|  | 0987 | ReactiveCos3 | I16 | 0.0001 |  | -10000 | 10000 | RW | 用于无功模式三，第三点功率因数值 | for reactive mode III, third point power factor value | Installers
|  | 0988 | ReactivedynamicValue3 | I16 | 1 | % | -100 | 100 | RW | 用于无功模式三，第三点功率百分比 | for reactive mode III, third point power percentage | Installers
|  | 0989 | ReactiveCos4 | I16 | 0.0001 |  | -10000 | 10000 | RW | 用于无功模式三，第四点功率因数值 | for reactive mode III, fourth power factor point | Installers
|  | 098A | ReactivedynamicValue4 | I16 | 1 | % | -100 | 100 | RW | 用于无功模式三，第四点功率百分比 | for reactive mode III, fourth power point percentage | Installers
|  | 098B | LockinV | U16 | 1 | % | 0 | 200 | RW | 用于无功模式三，LockinV电压数值百分比 | for reactive mode III, percentage of LockinV voltage value | Installers
|  | 098C | LockoutV | U16 | 1 | % | 0 | 200 | RW | 用于无功模式三，LockoutV电压数值百分比 | for reactive mode III, percentage of voltage value LockoutV | Installers
|  | 098D | HighVoltStartValue4 | U16 | 1 | % | 0 | 200 | RW | 用于无功模式四，高压起始电压百分比 | for reactive mode IV, percentage of high voltage starting voltage | Installers
|  | 098E | HighVoltEndValue4 | U16 | 1 | % | 0 | 200 | RW | 用于无功模式四，高压终止电压百分比 | for reactive mode IV, % of HV termination voltage | Installers
|  | 098F | LowVoltStartValue4 | U16 | 1 | % | 0 | 200 | RW | 用于无功模式四，低压起始电压百分比 | for reactive mode IV, % of LV starting voltage | Installers
|  | 0990 | LowVoltEndValue4 | U16 | 1 | % | 0 | 200 | RW | 用于无功模式四，低压终止电压百分比 | for reactive mode IV, % LV termination voltage | Installers
|  | 0991 | LockinPower4 | U16 | 1 | % | 0 | 100 | RW | 用于无功模式四，Lockin功率值百分比 | for reactive mode IV, % of Lockin power value | Installers
|  | 0992 | LockoutPower4 | U16 | 1 | % | 0 | 100 | RW | 用于无功模式四，Lockout功率值百分比 | for reactive mode IV, % of Lockout power value | Installers
|  | 0993 | MaxLeadingReactivePower4 | U16 | 0.01 | %Pn | 0 | 10000 | RW | 用于无功模式四，最大超前无功功率百分比 | for reactive mode IV, % of maximum overrun reactive power | Installers
|  | 0994 | ReactiveResponseWaitTime4 | U16 | 10 | ms | 0 | 65535 | RW | 用于无功模式四，无功响应等待时间 | for Reactive mode IV, Reactive response waiting time | Installers
|  | 0995 | ReactivePowerOffset4 | I16 | 0.01 | %Qmax | -10000 | 10000 | RW | 用于无功模式四，无功功率偏移量百分比。在整个运行电压范围内偏移无功曲线。正值表示超前，负值表示滞后。 | For reactive mode IV, percentage reactive power offset Offset reactive power curve over the entire operating voltage range. Positive values indicate overrunning, negative values indicate lagging. | Installers
|  | 0996 | ReactivePowerStart4 | U16 | 0.01 | %Pn | -10000 | 10000 | RW | 用于无功模式四，低压起始电压至高压起始电压点无功功率变化范围百分比的50%。低压起始电压对应该寄存器滞后的无功功率；高压起始电压对应该寄存器超前的无功功率； | For reactive mode IV, 50% of the percentage change in reactive power range from the low voltage starting voltage to the high voltage starting voltage point. The low-voltage starting voltage corresponds to the reactive power lagging in this register; the high-voltage starting voltage corresponds to the reactive power overrunning in this register; | Installers
|  | 0997 | HighVoltStartValue5 | U16 | 1 | % | 0 | 200 | RW | 用于无功模式五，高压起始电压百分比 | For reactive mode V, percentage of high-voltage starting voltage | Installers
|  | 0998 | HighVoltEndValue5 | U16 | 1 | % | 0 | 200 | RW | 用于无功模式五，高压终止电压百分比 | for reactive mode V, percentage of high-voltage termination voltage | Installers
|  | 0999 | LowVoltStartValue5 | U16 | 1 | % | 0 | 200 | RW | 用于无功模式五，低压起始电压百分比 | for reactive mode V, percentage of low-voltage starting voltage | Installers
|  | 099A | LowVoltEndValue5 | U16 | 1 | % | 0 | 200 | RW | 用于无功模式五，低压终止电压百分比 | for reactive mode V, percentage of LV termination voltage | Installers
|  | 099B | LockinPower5 | U16 | 1 | % | 0 | 100 | RW | 用于无功模式五，Lockin功率值百分比 | for reactive mode V, percentage of Lockin power value | Installers
|  | 099C | LockoutPower5 | U16 | 1 | % | 0 | 100 | RW | 用于无功模式五，Lockout功率值百分比 | for reactive mode V, % Lockout power value | Installers
|  | 099D | MaxReactivePower5 | U16 | 0.01 | % | 0 | 10000 | RW | 用于无功模式五，最大无功功率百分比 | for reactive mode V, % of maximum reactive power | Installers
|  | 099E | ReactiveResponseWaitTime5 | U16 | 10 | ms | 0 | 65535 | RW | 用于无功模式五，无功响应等待时间 | for reactive mode V, Reactive response waiting time | Installers
|  | 099F | PhaseType | U16 |  |  | 0 | 2 | RW | 用于无功模式六，相位类型 0：零无功功率 1：滞后无功功率 2：超前无功功率 | for reactive mode VI, phase type 0: Zero reactive power 1: hysteresis reactive power 2: overrun reactive power | Installers
|  | 09A0 | ReactiveResponsePeriod | U16 | 1 | 秒 | 1 | 65535 | RW | 用于无功（1、2、3、4、5、6）设置无功调节时长 | For reactive power (1, 2, 3, 4, 5, 6) Set reactive power regulation time | Installers
|  | 09A1 | MaxLaggingReactivePower4 | U16 | 0.01 | %Pn | 0 | 10000 | RW | 无功模式四，最大滞后无功功率百分比 | Reactive mode IV, maximum hysteresis reactive power percentage | Installers
3.8Voltage crossing parameters(0x09C0-0x09FF)
|  | 09C0 | VRTConfig | U16 |  |  |  |  | RW | Bit0：LVRT使能位 Bit1：OVRT使能位 Bit2：零电流模式使能位 Bit3：继承穿越前无功电流 Bit4：使用跌落前的电压计算电流 Bit5：负序电流使能位 Bit6：高穿有功使能位 Bit8-11：电压穿越电流计算模式 补充：1. LVRT/OVRT/零电流模式/负序电流/高穿有功的使能位，使能位是对应功能的开关，置为1使能(开),置为0禁止(关)。 注：负序电流使能位和高穿有功使能位不能体现。 | Bit0: LVRT enable bit Bit1: OVRT enable bit Bit2: Zero current mode enable bit Bit3: Inherit pre-crossover reactive current Bit4: Current calculation using pre-drop voltage Bit5: Negative sequence current enable bit Bit6: High-through active enable bit Bit8-11: Voltage crossing current calculation mode Note: 1. The enable bits for LVRT/OVRT/zero current mode/negative sequence current/high throughput active are switches for the corresponding function, set to 1 to enable (on), set to 0 to disable (off). Note: The negative sequence current enable bit and the high through active enable bit cannot be reflected. | Installers | [6 empty] | LVRT使能位控制着进入LVRT电压值百分比和寄存器地址（0x09C2-0x09CC）功能。 OVRT使能位控制着地址（0x09CD-0x09D8）寄存器功能。 零电流模式使能位：控制着零电流模式进入低/高电压百分比。继承穿越前无功电流控制着低/高压穿越退出电压值百分比、低/高压穿越无功电流计算起始电压值百分比。 只有相关使能位打开，对应寄存器的功能才能体现。 | The LVRT enable bit controls access to the LVRT voltage value percentage and register address (0x09C2-0x09CC) functions. The OVRT enable bit controls the address (0x09CD-0x09D8) register function. Zero current mode enable bit: controls the zero current mode into the low/high voltage percentage. The reactive current before inheritance crossing controls the low/high crossing exit voltage value percentage and the low/high crossing reactive current calculation starting voltage value percentage. The function of the corresponding register is only available if the relevant enable bit is switched on.
|  | 09C1 | LvrtInVolt | U16 | 1 | % | 0 | 65535 | RW | 进入LVRT电压值百分比 | Percentage of voltage value entering LVRT | Installers | [6 empty] | 1. 0x09C0-bit0:LVRT使能位有关 置为1使能(开),置为0禁止(关) | 1. 0x09C0-bit0:LVRT enable bit related Set to 1 to enable (on), set to 0 to disable (off)
|  | 09C2 | LvrtFirstPointVolt | U16 | 1 | % | 0 | 65535 | RW | 低压穿越第一点电压百分比 | Low voltage crossing first point voltage percentage | Installers
|  | 09C3 | LvrtFirstPointTime | U16 | 1 | ms | 0 | 65535 | RW | 低压穿越第一点时间 | Low voltage crossing first point time | Installers
|  | 09C4 | LvrtSecondPointVolt | U16 | 1 | % | 0 | 65535 | RW | 低压穿越第二点电压百分比 | Low voltage crossing second point voltage percentage | Installers
|  | 09C5 | LvrtSecondPointTime | U16 | 1 | ms | 0 | 65535 | RW | 低压穿越第二点时间 | Low voltage crossing second point time | Installers
|  | 09C6 | LvrtThirdPointVolt | U16 | 1 | % | 0 | 65535 | RW | 低压穿越第三点电压百分比 | Percentage of LVRT crossing third point voltage | Installers
|  | 09C7 | LvrtThirdPointTime | U16 | 1 | ms | 0 | 65535 | RW | 低压穿越第三点时间 | Low voltage crossing point 3 time | Installers
|  | 09C8 | LvrtFourthPointVolt | U16 | 1 | % | 0 | 65535 | RW | 低压穿越第四点电压百分比 | Low voltage crossing point 4 % voltage | Installers
|  | 09C9 | LvrtFourthPointTime | U16 | 1 | ms | 0 | 65535 | RW | 低压穿越第四点时间 | Low voltage crossing fourth point time | Installers
|  | 09CA | LvrtReactiveCurrentCoefficientK | U16 | 0.1 | p.u. | 0 | 65535 | RW | 低压穿越无功电流系数K | Low voltage crossing reactive current factor K | Installers
|  | 09CB | LvrtWaitingTimeAfterVoltageRecovery | U16 | 1 | ms | 0 | 65535 | RW | 低压穿越恢复后的等待时间 | Waiting time after low voltage crossing recovery | Installers
|  | 09CC | LvrtPowerBackRate | U16 | 1 | %Pn/min | 1 | 300 | RW | 低压穿越功率回载速率 | Low voltage crossing power return rate | Installers
|  | 09CD | OvrtInVlot | U16 | 1 | % | 0 | 65535 | RW | 进入OVRT电压值百分比 | Percentage of voltage value into OVRT | Installers | [6 empty] | 1. 0x09C0-bit1:OVRT使能位有关 置为1使能(开),置为0禁止(关) | 1. 0x09C0-bit1: OVRT enable bit related Set to 1 to enable (on), set to 0 to disable (off)
|  | 09CE | OvrtFirstPointVolt | U16 | 1 | % | 0 | 65535 | RW | 高压穿越第一点电压百分比 | Low voltage crossing first point voltage percentage | Installers
|  | 09CF | OvrtFirstPointTime | U16 | 10 | ms | 0 | 65535 | RW | 高压穿越第一点时间 | High voltage crossing first point time | Installers
|  | 09D0 | OvrtSecondPointVolt | U16 | 1 | % | 0 | 65535 | RW | 高压穿越第二点电压百分比 | Percentage of voltage at second point of high voltage crossing | Installers
|  | 09D1 | OvrtSecondPointTime | U16 | 10 | ms | 0 | 65535 | RW | 高压穿越第二点时间 | High voltage crossing second point time | Installers
|  | 09D2 | OvrtThirdPointVolt | U16 | 1 | % | 0 | 65535 | RW | 高压穿越第三点电压百分比 | Percentage of high voltage crossing third point voltage | Installers
|  | 09D3 | OvrtThirdPointTime | U16 | 10 | ms | 0 | 65535 | RW | 高压穿越第三点时间 | High voltage crossing point 3 time | Installers
|  | 09D4 | OvrtFourthPointVolt | U16 | 1 | % | 0 | 65535 | RW | 高压穿越第四点电压百分比 | Percentage of high voltage crossing point 4 | Installers
|  | 09D5 | OvrtFourthPointTime | U16 | 10 | ms | 0 | 65535 | RW | 高压穿越第四点时间 | High voltage crossing fourth point time | Installers
|  | 09D6 | OvrtReactiveCurrentCoefficientK | U16 | 0.1 | p.u. | 0 | 65535 | RW | 高压穿越无功电流系数K | High voltage crossing reactive current factor K | Installers
|  | 09D7 | OvrtWaitingTimeAfterVoltageRecovery | U16 | 1 | ms | 0 | 65535 | RW | 高压穿越恢复后的等待时间 | Waiting time after high voltage crossing recovery | Installers
|  | 09D8 | OvrtPowerBackRate | U16 | 1 | %Pn/min | 1 | 300 | RW | 高压穿越功率回载速率 | High voltage crossing power return rate | Installers
|  | 09D9 | ZeroCurrentModeInLowVolt | U16 | 1 | % | 0 | 65535 | RW | 零电流模式进入低电压百分比 | Zero current mode into low voltage percentage | Installers
|  | 09DA | ZeroCurrentModeInHighVolt | U16 | 1 | % | 0 | 65535 | RW | 零电流模式进入高电压百分比 | Zero-current mode entry high voltage percentage | Installers
|  | 09DB | LvrtOutVolt | U16 | 1 | % | 0 | 65535 | RW | 低压穿越退出电压值百分比 | Low voltage crossing exit voltage value percentage | Installers
|  | 09DC | LvrtIqVoltStart | U16 | 1 | % | 0 | 65535 | RW | 低压穿越无功电流计算起始电压值百分比 | Percentage of starting voltage value for low voltage ride-through reactive current calculation | Installers
|  | 09DD | OvrtOutVolt | U16 | 1 | % | 0 | 65535 | RW | 高压穿越退出电压值百分比 | Percentage of high voltage crossing exit voltage value | Installers
|  | 09DE | OvrtIqVoltStart | U16 | 1 | % | 0 | 65535 | RW | 高压穿越无功电流计算起始电压值百分比 | Percentage of calculated starting voltage value for high voltage crossing reactive current | Installers
|  | 09DF | MaxUnbalanceIqPct | U16 | 1 | % | 0 | 65535 | RW | 不平衡穿越最大无功电流百分比 | Percentage of maximum reactive current for unbalanced crossing | Installers
|  | 09E0 -- 09FF | [7 empty] | 预留 | Reserved
3.9Isolated Island、GFCI、ISO parameters(0x0A00-0x0A3F)
|  | 0A00 | IslandConfig | U16 |  |  |  |  | RW | Bit0：孤岛使能寄存器 Bit1：单相孤岛使能（用于三相逆变器） | Bit0: islanding enable register Bit1: Single-phase islanding enable (for 3-phase inverters) | Installers | [6 empty] | 绝缘阻抗使能寄存器：控制着绝缘阻抗保护值和组件对地泄露电流限制，这两个寄存器的值乘积是一个设定的定值； GFCI使能寄存器：为漏电流限制（暂不开放，设置无效）的开关，但漏电流限制寄存器不能写入值，程序中写死了； | Insulation impedance enable register: controls the insulation impedance protection value and the component leakage current limit to ground, the product of the two register values is a set fixed value; GFCI enable register: a switch for the leakage current limit (temporarily not open, setting invalid), but the leakage current limit register cannot write values, the program is written dead;
|  | 0A01 | GFCIConfig | U16 |  |  |  |  | RW | Bit0：GFCI使能寄存器 | Bit0: GFCI enable register | Installers
|  | 0A02 | ISOConfig | U16 |  |  |  |  | RW | Bit0：绝缘阻抗使能寄存器 Bit1：接地检测使能寄存器 | Bit0: Insulation impedance enable register Bit1: earth detection enable register | Installers
|  | 0A03 | InsulationProtectionValue | U16 | 1 | kΩ | 30 | 65535 | RW | 绝缘阻抗保护值 | Insulation impedance protection value | Installers
|  | 0A04 | IsoLeakageCurrentLimit | U16 | 1 | mA | 1 | 50 | RW | 组件对地泄露电流限制 | Component to ground leakage current limit | Installers
|  | 0A05 | GFCILimit | U16 | 1 | mA/kVA | 1 | 50 | RW | 漏电流限制（暂不开放，设置无效） | Leakage current limit (temporarily not open, setting invalid) | Installers
|  | 0A06 | PE_N_Config | U16 |  |  |  |  | RW | PE和N控制寄存器 Bit0：离网PEN短接使能位 Bit1：N线检测使能位 | PE and N control registers Bit0: Off-grid PEN short enable bit Bit1: N line detection enable bit | Installers
|  | 0A07 | IslandDetectSensitivity | U16 |  |  |  |  | RW | 孤岛检测敏感度 | Sensitivity to islanding detection | Installers
|  | 0A08 | PEProtectionValue | U16 | 1 | kΩ | 1000 | 65535 | RW | 接地故障判断阈值 | Ground fault judgement threshold | Installers
|  | 0A09 -- 0A3F | [7 empty] | 预留 | Reserved
3.10Pulling an arc(0x0A40-0x0A7F)
|  | 0A40 -- 0A7F | [7 empty] | 预留 | Reserved
四、Parameter setting area(0x1000-0x17FF)
4.1Basic configuration(0x1000-0x10FF)
|  | 1000 -- 1003 | AddressMask_Config_Basic1 | U64 |  |  |  |  | R | 本地址开始的64个寄存器地址字的掩码区。 参看地址0x0040的说明 | Mask area for the 64 register address words starting at this address. Refer to the description of address 0x0040 | End-users | 00000000 | 0000000F |  |  |  |  | 用于区分哪些地址有效，哪些地址无效，主要作用就是不同机型使用的寄存器不同，通过掩码做区分。此块区域支持任意读取。 | It is used to distinguish which addresses are valid and which are not. The main function is that different models use different registers and are distinguished by a mask. This area can be read at will.
系统时间 2-2 | System Time 2-2 | 1004 | SysTimeConfig_Year | U16 |  | 年 | 0 | 99 | RW | 系统时间-年份； 实际年份等于2000+寄存器值 | System time - year; Actual year equals 2000 + register value | End-users | [6 empty] | 写入时，固定的首地址为0x1004，长度为7。写入数据保存在EEPORM。 | When writing, the first address is fixed at 0x1004 and the length is 7. The written data is stored in the EEPORM.
|  | 1005 | SysTimeConfig_Month | U16 |  | 月 | 1 | 12 | RW | 系统时间-月份 | System time - month | End-users
|  | 1006 | SysTimeConfig_Date | U16 |  | 日 | 1 | 31 | RW | 系统时间-日分 | System time - minutes of day | End-users
|  | 1007 | SysTimeConfig_Hour | U16 |  | 时 | 0 | 23 | RW | 系统时间-小时 | System time - hour | End-users
|  | 1008 | SysTimeConfig_Minute | U16 |  | 分 | 0 | 59 | RW | 系统时间-分钟 | System time-minute | End-users
|  | 1009 | SysTimeConfig_Second | U16 |  | 秒 | 0 | 59 | RW | 系统时间-秒 | System time-second | End-users
|  | 100A | SysTimeConfig_Control | U16 |  |  | 1 | 1 | RW | 写入值为1时，系统时间影子寄存器中的值更新到实际系统时间； 读取时，返回上次写入操作的状态： 0x0000：成功 0x0001：正在操作 0xFFFB：操作失败，控制器拒绝响应（可能控制器正忙或配置错误） 0xFFFC：操作失败，控制器无应答 0xFFFD：操作失败，当前功能被禁止 0xFFFE：操作失败，参数存取失败 0xFFFF：操作失败，输入参数有误 | On a write value of 1, the value in the system time shadow register is updated to the actual system time; On a read, the status of the last write operation is returned: 0x0000: successful 0x0001: operation in progress 0xFFFB: operation failed, controller refused to respond (possibly controller is busy or misconfigured) 0xFFFC: operation failed, no response from the controller 0xFFFD: operation failed, current function is disabled 0xFFFE: operation failed, parameter access failed 0xFFFF: operation failed, input parameters incorrect | End-users
RS485参数设置 | RS485 parameter setting | 100B | RS485Config_Address | U16 |  |  | 1 | 247 | RW | RS485配置-地址 | RS485 configuration - address | End-users | [6 empty] | 写入时，固定的首地址为0x100B，长度为5。 | When writing in, the fixed first address is 0x100B and the length is 5.
|  | 100C | RS485Config_Baud | U16 |  |  | 0 | 4 | RW | RS485波特率选择； 0：4800bps 1：9600bps（默认） 2：19200bps 3：38400bps 4：57600bps 5：115200bps 10：1200bps 11：2400bps | RS485 baud rate selection; 0: 4800bps 1: 9600bps (default) 2: 19200bps 3: 38400bps 4: 57600bps 5: 115200bps 10: 1200bps 11: 2400bps | End-users
|  | 100D | RS485Config_StopBit | U16 |  |  | 0 | 2 | RW | RS485停止位选择； 0：1位停止位（默认） 1：1.5位停止位 2：2位停止位 | RS485 stop bit selection; 0: 1 bit stop bit (default) 1: 1.5 bit stop bit 2: 2-bit stop bit | End-users
|  | 100E | RS485Config_ParityBit | U16 |  |  | 0 | 4 | RW | RS485校验位选择； 0：无校验/None（默认） 1：偶校验/Even 2：奇校验/Odd 3：高/Mark 4：低/Space | RS485 parity bit selection; 0: No parity/None (default) 1: Even parity/Even 2: Odd parity/Odd 3: High/Mark 4: Low/Space | End-users
|  | 100F | RS485Config_Control | U16 |  |  | 1 | 1 | RW | 写入值为1时，RS485配置影子寄存器中的值更新到系统RS485配置中； 读取时，返回上次写入操作的状态： 0x0000：成功 0x0001：正在操作 0xFFFB：操作失败，控制器拒绝响应（可能控制器正忙或配置错误） 0xFFFC：操作失败，控制器无应答 0xFFFD：操作失败，当前功能被禁止 0xFFFE：操作失败，参数存取失败 0xFFFF：操作失败，输入参数有误 | On a write value of 1, the value in the RS485 configuration shadow register is updated to the system RS485 configuration; When reading, the status of the last write operation is returned: 0x0000: successful 0x0001: operation in progress 0xFFFB: operation failed, controller refused to respond (possibly the controller is busy or misconfigured) 0xFFFC: operation failed, no response from the controller 0xFFFD: operation failed, current function is disabled 0xFFFE: operation failed, parameter access failed 0xFFFF: operation failed, wrong input parameter | End-users
PV输入模式设置 | PV input mode setting | 1010 | PV_InputMode_Config | U16 |  |  | 0 | 1 | RW | PV输入模式选择； 0：并联模式 1：独立模式（默认） | PV input mode selection; 0: parallel mode 1: independent mode (default) | Installers | [6 empty] | 写入时，此地址为固定的首地址，长度为1。此设置和下面的输入通道类型选择在一种机型上只会有一个。 | When writing, this address is a fixed first address of length 1. This setting and the input channel type selection below will only be one on a model.
|  | 1011 -- 1020 | InputType_Channel0_Config -- InputType_Channel15_Config | U16 |  |  | 0 | 255 | RW | 输入通道0-15类型选择（16个）； 值0表示当前通道不使用； 值1～127表示当前通道为光伏电池板输入； 值128~255表示当前通道为蓄电池输入； 若两个或两个以上通道的值相同且大于零，表示这些通道并联输入； | Input channel 0-15 type selection (16); The value 0 indicates that the current channel is not in use; Values 1 to 127 indicate that the current channel is a PV panel input; values 128 to 255 indicate that the current channel is a battery input; If two or more channels have the same value and are greater than zero, it means that these channels are input in parallel; | Installers | [6 empty] | 写入时，固定的首地址为0x1011，长度为1到17的任意值，不同的机型输入通道不同，按实际的输入通道选择即可。 并且输入通道的修改均要在逆变器不处于并网或离网状态。 | When writing, the fixed first address is 0x1011 and the length is any value from 1 to 17. The input channel varies from model to model, so select the actual input channel. And the input channels are all modified when the inverter is not on or off-grid.
|  | 1021 | InputType_Control | U16 |  |  | 1 | 1 | RW | 写入值为1时，输入通道类型影子寄存器中的值更新到系统输入通道类型配置中； 读取时，返回上次写入操作的状态： 0x0000：成功 0x0001：正在操作 0xFFFB：操作失败，控制器拒绝响应（可能控制器正忙或配置错误） 0xFFFC：操作失败，控制器无应答 0xFFFD：操作失败，当前功能被禁止 0xFFFE：操作失败，参数存取失败 0xFFFF：操作失败，输入参数有误 | the value in the input channel type shadow register is updated to the system input channel type configuration when the write value is 1; On a read, the status of the last write operation is returned as follows: 0x0000: successful 0x0001: operation in progress 0xFFFB: operation failed, controller refused to respond (possibly controller is busy or misconfigured) 0xFFFC: operation failed, no response from the controller 0xFFFD: operation failed, current function is disabled 0xFFFE: operation failed, parameter access failed 0xFFFF: operation failed, wrong input parameter | Installers
从U盘中取出安规参数 | Safety parameters from USB stick | 1022 | SafetyUpdateFromUSB_Control | U16 |  |  | 1 | 1 | RW | 写入值为1时，用于通讯板从U盘中取出安规参数； 读取时，返回上次写入操作的状态： 0x0000：成功 0x0001：正在操作 0xFFFB：操作失败，控制器拒绝响应（可能控制器正忙或配置错误） 0xFFFC：操作失败，控制器无应答 0xFFFD：操作失败，当前功能被禁止 0xFFFE：操作失败，参数存取失败 0xFFFF：操作失败，输入参数有误 | write value of 1 for the communication board to remove the safety parameters from the USB stick; When reading, the status of the last write operation is returned: 0x0000: successful 0x0001: operation in progress 0xFFFB: operation failed, controller refused to respond (possibly controller is busy or misconfigured) 0xFFFC: operation failed, no response from the controller 0xFFFD: operation failed, current function is disabled 0xFFFE: operation failed, parameter access failed 0xFFFF: operation failed, wrong input parameter | Installers | [6 empty] | 暂未开放写入，只支持读取 | Not yet open for writing, only for reading
防逆流 | Backflow prevention | 1023 | AntiReflux_Control | U16 |  |  | 0 | 2 | RW | 防逆流使能控制 0：禁止防逆流功能 1：默认防逆流模式 2：三相平均功率防逆流模式 3：相功率模式 | Anti-backflow enable control 0: Anti-backflow function disabled 1: default anti-backflow mode 2: three-phase average power anti-current mode 3: Phase power mode | Installers | [6 empty] | 写入时，固定的首地址为0x1023，长度为2 | Write with a fixed first address of 0x1023 and a length of 2
|  | 1024 | AntiReflux_Power | U16 | 100 | W | 0 | 65535 | RW | 防逆流功率 | Anti-backflow power | Installers
IV曲线扫描设置 | IV curve scan settings | 1025 | IVCurveScan_Control | U16 |  |  | 0 | 1 | RW | IV曲线扫描使能控制 | IV curve scan enable control | Installers | [6 empty] | 写入时，固定的首地址为0x1025，长度为2 | Write, fixed first address 0x1025, length 2
|  | 1026 | IVCurveScan_Period | U16 | 1 | 分钟 | 5 | 65535 | RW | IV曲线扫描周期 | IV curve scan cycle | Installers
|  | 1027 | IVCurveScan_Oneshot | U16 |  |  | 1 | 1 | RW | IV曲线扫描激活； 写入值为1时，激活1次IV曲线扫描； 读取时，返回上次写入操作的状态： 0x0000：成功 0x0001：正在操作 0xFFFB：操作失败，控制器拒绝响应（可能控制器正忙或配置错误） 0xFFFC：操作失败，控制器无应答 0xFFFD：操作失败，当前功能被禁止 0xFFFE：操作失败，参数存取失败 0xFFFF：操作失败，输入参数有误 | IV curve scan activation; Activation of 1 IV curve scan for a write value of 1; On a read, returns the status of the last write operation to 0x0000: successful 0x0001: operation in progress 0xFFFB: operation failed, controller refused to respond (possibly controller is busy or misconfigured) 0xFFFC: operation failed, no response from the controller 0xFFFD: operation failed, current function is disabled 0xFFFE: operation failed, parameter access failed 0xFFFF: operation failed, wrong input parameter | Installers | [6 empty] | 写入时，固定的首地址为0x1027，长度为1 | Write with a fixed first address of 0x1027 and a length of 1
|  | 1028 | IVCurveScan_ReadChannel | U16 |  |  | 0 | 31 | RW | IV曲线扫描回传数据通道。 该寄存器用于指定IV曲线扫描结果回传值所对应的PV通道。 | IV curve scan return data channel. This register is used to specify the PV channel corresponding to the return value of the IV curve scan result. | Installers | [6 empty] | 写入时，固定的首地址为0x1028，长度为1，写入值不能超过逆变器最大的PV通道 | Write with a fixed first address of 0x1028 and a length of 1. The write value cannot exceed the maximum PV channel of the inverter
应急供电 | Emergency power supply | 1029 | EPS_Control | U16 |  |  | 0 | 2 | RW | 应急供电使能控制 0：关闭应急供电(默认) 1：开启应急供电，禁止冷启动 2：开启应急供电，使能冷启动 | Emergency power supply enable control 0: turn off emergency power supply (default) 1: Enable emergency power supply, disable cold start 2: emergency power on, cold start enabled | End-users | [6 empty] | 写入时，固定的首地址为0x1029，长度为2 | When writing, the fixed first address is 0x1029 and the length is 2
|  | 102A | EPS_WaitTime | U16 | 1 | 秒 | 0 | 65535 | RW | 应急供电启动等待时间（预留功能） | Emergency power supply start-up waiting time (reserved function) | End-users
电池激活 | Battery activation | 102B | BatteryActive_Control | U16 |  |  | 0 | 1 | RW | 电池自动激活使能控制 | Automatic battery activation enable control | End-users | [6 empty] | 写入时，固定的首地址为0x102b，长度为2 | When writing, the fixed first address is 0x102b and the length is 2
|  | 102C | BatteryActive_Oneshot | U16 |  |  | 1 | 1 | RW | 电池激活； 写入值为1时，进行1次电池激活； 读取时，返回上次写入操作的状态： 0x0000：成功 0x0001：正在操作 0xFFFB：操作失败，控制器拒绝响应（可能控制器正忙或配置错误） 0xFFFC：操作失败，控制器无应答 0xFFFD：操作失败，当前功能被禁止 0xFFFE：操作失败，参数存储失败 0xFFFF：操作失败，输入参数有误 | Battery activation; 1 battery activation for a write value of 1; On read, return to the status of the last write operation at 0x0000: successful 0x0001: operation in progress 0xFFFB: operation failed, controller refused to respond (possibly controller is busy or misconfigured) 0xFFFC: operation failed, no response from the controller 0xFFFD: operation failed, current function is disabled 0xFFFE: operation failed, parameter storage failed 0xFFFF: operation failed, wrong input parameters | End-users
CT自动校正 | CT Auto Calibration | 102D | CT_Auto_Calibrate | U16 |  |  | 1 | 1 | RW | CT自动校正； 写入值为1时，进行1次CT自动校正； 读取时，返回上次写入操作的状态： 0x0000：成功 0x0001：正在操作 0xFFFB：操作失败，控制器拒绝响应（可能控制器正忙或配置错误） 0xFFFC：操作失败，控制器无应答 0xFFFD：操作失败，当前功能被禁止 0xFFFE：操作失败，参数存储失败 0xFFFF：操作失败，输入参数有误 | Automatic CT correction; 1 CT auto-correction for a write value of 1; When reading, return to the status of the last write operation: 0x0000: success 0x0001: operation in progress 0xFFFB: operation failed, controller refused to respond (possibly controller is busy or misconfigured) 0xFFFC: operation failed, no response from the controller 0xFFFD: operation failed, current function is disabled 0xFFFE: operation failed, parameter storage failed 0xFFFF: operation failed, wrong input parameters | Installers | [6 empty] | 写入时，固定的首地址为0x102D，长度为1 | Write with a fixed first address of 0x102D and a length of 1
意大利自动测试 | Italy Auto Test | 102E | Italy_AutoTest | U16 |  |  | 1 | 2 | RW | 意大利自动测试 写入： 0x0001：执行标准测试(S)； 0x0002：执行快速测试(F)； 读取时，返回上次写入操作的状态： 0x0000：成功 0x0001：正在操作标准测试 0x0002：正在操作快速测试 0xFFFB：操作失败，控制器拒绝响应（可能控制器正忙或配置错误） 0xFFFC：操作失败，控制器无应答 0xFFFD：操作失败，当前功能被禁止 0xFFFE：操作失败，参数存储失败 0xFFFF：操作失败，输入参数有误 | Italian automatic test Write to: 0x0001: execution of a standard test (S); 0x0002: execution of a fast test (F); When reading, return the status of the last write operation: 0x0000: success 0x0001: standard test being operated 0x0002: fast test being operated 0xFFFB: operation failed, controller refused to respond (possibly controller is busy or misconfigured) 0xFFFC: operation failed, no response from the controller 0xFFFD: operation failed, current function is disabled 0xFFFE: operation failed, parameter storage failed 0xFFFF: operation failed, wrong input parameter | Installers | [6 empty] | 写入时，固定的首地址为0x102E，长度为1 | Write with fixed first address 0x102E and length 1
|  | 102F | [7 empty] | 预留 | Reserved
电能统计回传 | Electrical energy statistics return | 1030 | EnergyStatistics_Date_Year | U16 | 1 | 年 | 0 | 19 | RW | 电能统计回传日期设置寄存器。 该寄存器指定回传的电能数据的年份。年份指相对逆变器系统时间最近第N年。N为寄存器值。 0：系统时间当年； 1：系统时间前1年； … 19：系统时间前19年。 | The electrical energy statistics return date setting register. This register specifies the year of the electrical energy data to be returned. The year refers to the most recent Nth year relative to the inverter system time. n is the register value. 0: the current year of system time; 1: 1 year before system time; ... 19: 19 years before system time. | Installers | [6 empty] | 这四个寄存器需要一起使用，用于读取当前或者以前的电量数据。读出的数据保存在地址0x1610到0x165F区域。 写入时，固定的首地址为0x1030，长度为4 | These four registers need to be used together to read the current or previous power data. The read data is stored in the area of addresses 0x1610 to 0x165F. When writing in, the fixed first address is 0x1030 and the length is 4
|  | 1031 | EnergyStatistics_Date_Month | U16 | 1 | 月 | 1 | 12 | RW | 电能统计回传日期设置寄存器。 该寄存器指定回传的电能数据的月份。 | Electrical energy statistics return date setting register. This register specifies the month for which the electrical energy data is to be returned. | Installers
|  | 1032 | EnergyStatistics_Date_Date | U16 | 1 | 日 | 1 | 31 | RW | 电能统计回传日期设置寄存器。 该寄存器指定回传的电能数据的日分。 | Electrical energy statistics return date setting register. This register specifies the day minute of the returned electrical energy data. | Installers
|  | 1033 | EnergyStatistics_Config | U16 |  |  |  |  | RW | 电能统计回传设置寄存器。 高字节：回传数据的日期时间设置。 0x01：每日，回传区前24条数据有效； 0x02：每月，回传区前31条数据有效； 0x03：每年，回传区前12条数据有效； 0x04：生命周期，回传区前20条数据有效； 其他：无效。 低字节：回传数据的物理量设置。 0x01：光伏发电量； 0x02：负载耗电量； 0x03：系统买电量； 0x04：系统卖电量； 0x05：电池充电量； 0x06：电池放电量； 其他：无效。 | Electric energy statistics return set register. High byte: date time setting for the return data. 0x01: daily, the first 24 data entries in the return area are valid; 0x02: monthly, the first 31 data in the return area are valid; 0x03: per year, the first 12 data in the echo area are valid; 0x04: life cycle, valid for the first 20 data in the return area; Others: invalid. Low byte: physical quantity setting for the return data. 0x01: amount of electricity generated by the PV; 0x02: load power consumption; 0x03: system buy power; 0x04: amount of electricity sold by the system; 0x05: amount of battery charging; 0x06: amount of battery discharging; Other: invalid. | Installers
语言 | Languages | 1034 | Language | U16 |  |  | 0 | 65535 | RW | 逆变器菜单语言编号设置寄存器。 0：中文 1：英文 2：意大利文 3：德文 4：法文 5：葡萄牙文 6：乌克兰文 7：斯洛伐克文 8：西班牙文 9：芬兰文 10：波兰文 11：韩文 12：日文 13：俄文 14：捷克语 | Inverter menu language number setting register. 0: Chinese 1: English 2: Italian 3: German 4: French 5: Portuguese 6: Ukrainian 7: Slovak 8: Spanish 9: Finnish 10: Polish 11: Korean 12: Japanese 13: Russian 14: Czech | End-users | [6 empty] | 写入时，固定的首地址为0x1034，长度为1 | When writing, the fixed first address is 0x1034 and the length is 1.
并机控制 | Parallel control | 1035 | Parallel_Control | U16 |  |  | 0 | 2 | RW | 0：禁用并机功能 1：使能AC并机功能 2：使能AC+BAT并机功能 | 0: Disable parallel function 1: Enables the AC parallel function 2: Enables the AC+BAT parallel function | Installers | [6 empty] | 写入时，固定的首地址为0x1035，长度为3，不同机型的并机功能可能不一样，要根据实际机型设置。 | When writing, the fixed first address is 0x1035 and the length is 3. The parallel function may vary from model to model and should be set according to the actual model.
|  | 1036 | Parallel_Master_Slave | U16 |  |  | 0 | 1 | RW | 0：本机配置为从机 1：本机配置为主机（默认） | 0: This machine is configured as slave 1: This machine is configured as a master (default) | Installers
|  | 1037 | Parallel_Address | U16 |  |  | 0 | 10 | RW | 本机并机地址 | Local parallel address | Installers
3相4线模式电网不平衡支撑控制 | 3 phase 4 wire mode grid unbalance support control | 1038 | UnbalancedSupport_Control | U16 |  |  | 0 | 1 | RW | 3相4线模式电网不平衡支撑控制寄存器 0：禁用不平衡支撑功能（默认） 1：使能不平衡支撑功能 | 3 phase 4 wire mode grid imbalance support control register 0: Disable the unbalance support function (default) 1: enables the unbalance support function | Installers | [6 empty] | 写入时，固定的首地址为0x1038，长度为1 | When writing, the fixed first address is 0x1038 and the length is 1
电量倍率 | Power multiplier | 1039 | PV_Generation_Ratio | U16 | 0.001 | p.u. | 800 | 3600 | RW | 发电量倍率。默认值1000 | Power generation multiplier. Default value 1000 | Installers | [6 empty] | 暂未使用，可读取，但数据无意义 | Not in use, can be read, but data is meaningless
|  | 103A | Energy_Purchase_Ratio | U16 | 0.001 | p.u. | 800 | 1500 | RW | 买电量倍率。默认值1000 | Buy power multiplier. Default value 1000 | Installers
|  | 103B | Energy_Selling_Ratio | U16 | 0.001 | p.u. | 800 | 1500 | RW | 卖电量倍率。默认值1000 | Sell power multiplier. Default value 1000 | Installers
|  | 103C | Bat_Charge_Ratio | U16 | 0.001 | p.u. | 800 | 1500 | RW | 充电量倍率。默认值1000 | Charge amount multiplier. Default 1000 | Installers
|  | 103D | Bat_Discharge_Ratio | U16 | 0.001 | p.u. | 800 | 1500 | RW | 放电量倍率。默认值1000 | Discharge volume multiplier. Default value 1000 | Installers
逻辑接口控制 | Logic interface control | 103E | LogicInterface_Control | U16 |  |  | 0 | 1 | RW | 逻辑接口控制寄存器 0：禁用 1：使能 | Logical Interface Control Register 0: Disable 1: enable | Installers | [6 empty] | 写入时，固定的首地址为0x103E，长度为1 | When writing, the fixed first address is 0x103E, length 1
|  | 103F | [7 empty] | 预留 | Reserved
|  | 1040 -- 1043 | AddressMask_Config_Basic2 | U64 |  |  |  |  | R | 本地址开始的64个寄存器地址字的掩码区。 参看地址0x0040的说明 | Mask area for the 64 register address words starting at this address. Refer to the description of address 0x0040 | End-users | 00000000 | 0000000F |  |  |  |  | 用于区分哪些地址有效，哪些地址无效，主要作用就是不同机型使用的寄存器不同，通过掩码做区分。此块区域支持任意读取。 | It is used to distinguish which addresses are valid and which are not. The main purpose is to distinguish between different registers used by different models by means of a mask. This area can be read at will.
电池参数配置 | Battery configuration | 1044 | BatConfig_ID | U16 |  |  | 0 | 7 | RW | 电池序号。 该寄存器所指定的序号，与逆变器的实际的电池输入接口进行对应。 成功写入该寄存器后，电池参数将更新为所写入序号对应的参数。 | Battery serial number. The serial number specified in this register corresponds to the actual battery input interface of the inverter. After a successful write to this register, the battery parameters will be updated to the parameters corresponding to the written serial number. | End-users | [6 empty] | 当电池不为铅酸电池时，铅酸电池的默认参数无意义。 不同电池类型的参数有不同的限制且有些参数无法修改，使用默认值，具体参考电池说明文件 写入时，固定的首地址为0x1044，长度为1到23的任意值 | The default parameters for lead-acid batteries are meaningless when the battery is not a lead-acid battery. Different battery types have different limits and some parameters cannot be modified, use the default values, refer to the battery documentation for details When writing in, the fixed first address is 0x1044 and the length is any value from 1 to 23
|  | 1045 | BatConfig_Address | U16 |  |  | 0 | 99 | RW | 电池地址。 如果系统中允许接入多组电池，则该寄存器用于标记对应电池序号的物理接口的电池地址。 | Battery Address. If multiple batteries are allowed to be accessed in the system, this register is used to mark the battery address of the physical interface corresponding to the battery serial number. | End-users
|  | 1046 | BatConfig_Potocol | U16 |  |  | 0 | 65535 | RW | 电池参数-通讯协议 0：首航内置BMS/DEFAULT 1：派能协议/PYLON 2：首航协议/GENERAL 3：AMASS 4：LG 5：Alpha.ESS 6：CATL 7：Weco 8：Fronus 9：EMS 10：Nilar 11：BTS 5K 12：动为 | Battery parameters - communication protocol 0: First Flight built-in BMS/DEFAULT 1: Pie Energy protocol/PYLON 2: First flight protocol/GENERAL 3: AMASS 4: LG 5: Alpha.ESS 6: CATL 7: Weco 8: Fronus 9: EMS 10：Nilar 11: BTS 5K 12: Move for" | End-users
|  | 1047 | BatConfig_Voltage_Over | U16 | 0.1 | V | 0 | 65535 | RW | 电池参数-过压保护值 | Battery parameters - overvoltage protection value | Installers
|  | 1048 | BatConfig_Voltage_Charge | U16 | 0.1 | V | 0 | 65535 | RW | 电池参数-充电电压 | Battery parameters - charging voltage | Installers
|  | 1049 | BatConfig_Voltage_Lack | U16 | 0.1 | V | 0 | 65535 | RW | 电池参数-欠压保护电压 铅酸电池可见 | Battery parameters - undervoltage protection voltage Lead-acid batteries visible | Installers
|  | 104A | BatConfig_Voltage_Discharge_Stop | U16 | 0.1 | V | 0 | 65535 | RW | 电池参数-最低放电电压 | Battery parameters - minimum discharge voltage | Installers
|  | 104B | BatConfig_Current_Charge_Limit | U16 | 0.01 | A | 0 | 65535 | RW | 电池参数-最大充电电流限制 | Battery parameters - Maximum charge current limit | End-users
|  | 104C | BatConfig_Current_Discharge_Limit | U16 | 0.01 | A | 0 | 65535 | RW | 电池参数-最大放电电流限制 | Battery parameters - maximum discharge current limit | End-users
|  | 104D | BatConfig_Depth_of_Discharge | U16 | 1 | % | 1 | 90 | RW | DOD指示电网正常时的最大放电量，当SOC<1-DOD时逆变器停止放电，逆变器也会依据其他条件停止放电； DOD<=EOD | DOD indicates the maximum discharge when the grid is normal, the inverter stops discharging when SOC < 1 - DOD, the inverter also stops discharging depending on other conditions; DOD<=EOD | End-users
|  | 104E | BatConfig_End_of_Discharge | U16 | 1 | % | 1 | 90 | RW | EOD指示离网最大放电量，当SOC<1-EOD时逆变器停止放电，逆变器也会依据其他条件停止放电 | EOD indicates the maximum off-grid discharge, the inverter stops discharging when SOC<1-EOD, the inverter will also stop discharging according to other conditions | End-users
|  | 104F | BatConfig_Capacity | U16 | 1 | Ah | 1 | 65535 | RW | 电池参数-电池容量（默认50） | Battery parameters - battery capacity (default 50) | End-users
|  | 1050 | BatConfig_Voltage_Nominal | U16 | 0.1 | V | 0 | 65535 | RW | 电池参数-额定电池电压（默认0） | Battery parameters - rated battery voltage (default 0) | End-users
|  | 1051 | BatConfig_Cell_Type | U16 | 1 |  | 0 | 6 | RW | 电池参数-电芯类型； 0：铅酸（自定义） 1：磷酸铁锂 2：三元 3：钛酸锂 4：AGM 5：Gel 6：Flooded | Battery parameters - cell type; 0: Lead acid (custom) 1: Lithium iron phosphate 2: Ternary 3: Lithium titanate 4: AGM 5: Gel 6: Flooded | End-users
|  | 1052 | BatConfig_EPS_Buffer | U16 | 1 | % | 5 | 100 | RW | 电池参数-离网恢复放电回滞； EPS_Buffer不大于EOD | Battery parameters - off-grid recovery discharge hysteresis; EPS_Buffer not greater than EOD | End-users
|  | 1053 | BatConfig_Control | U16 |  |  |  |  | RW | 电池参数写入控制； 写入值为1时，电池参数影子寄存器中的值更新到系统电池参数配置中； 写入值为2时，电池参数影子寄存器中的值更新为BatConfig_Potocol的默认值； 读取时，返回上次写入操作的状态： 0x0000：成功 0x0001：正在操作 0xFFFB：操作失败，控制器拒绝响应（可能控制器正忙或配置错误） 0xFFFC：操作失败，控制器无应答 0xFFFD：操作失败，当前功能被禁止 0xFFFE：操作失败，参数存储失败 0xFFFF：操作失败，输入参数有误 | Battery parameter write control; A write value of 1 updates the value in the battery parameter shadow register to the system battery parameter configuration; a write value of 2 updates the value in the battery parameter shadow register to the default value of BatConfig_Potocol; On read, the status of the last write operation is returned: 0x0000: successful 0x0001: operation in progress 0xFFFB: operation failed, controller refused to respond (possibly controller is busy or misconfigured) 0xFFFC: operation failed, no response from the controller 0xFFFD: operation failed, current function is disabled 0xFFFE: operation failed, parameter storage failed 0xFFFF: operation failed, wrong input parameter | End-users
|  | 1054 | BatConfig_Address2 | U16 |  |  | 0 | 99 | RW | 电池地址2。 如果系统中允许接入多组电池，则该寄存器用于标记对应电池序号的物理接口的电池地址。 | Battery address 2. If multiple batteries are allowed to be accessed in the system, this register is used to mark the battery address of the physical interface corresponding to the battery serial number. | End-users
|  | 1055 | BatConfig_Address3 | U16 |  |  | 0 | 99 | RW | 电池地址3。 如果系统中允许接入多组电池，则该寄存器用于标记对应电池序号的物理接口的电池地址。 | Battery address 3. If multiple batteries are allowed to be accessed in the system, this register is used to mark the battery address of the physical interface corresponding to the battery serial number. | End-users
|  | 1056 | BatConfig_Address4 | U16 |  |  | 0 | 99 | RW | 电池地址4。 如果系统中允许接入多组电池，则该寄存器用于标记对应电池序号的物理接口的电池地址。 | Battery Address 4. If multiple batteries are allowed to be accessed in the system, this register is used to mark the battery address of the physical interface corresponding to the battery serial number. | End-users
|  | 1057 | BatConfig_TEMPCO | I16 | 0.1 | mV/Cell | -60 | 0 | RW | 电池参数-铅酸电池温度补偿系数。 | Battery Parameters-Lead Acid Battery Temperature Compensation Factor. | End-users
|  | 1058 | BatConfig_Voltage_Recovery_Buffer | U16 | 0.1 | V |  |  | RW | 电池参数-铅酸电池恢复放电电压增量。 如：“电池电压<最低放电电压”时停止放电； “电池电压>最低放电电压+恢复放电电压增量”时恢复放电。 | Battery parameters-Lead acid battery recovery discharge voltage increment. E.g. Battery voltage < minimum discharge voltage" to stop discharging; | End-users
|  | 1059 | BatConfig_Control_Bits | U16 |  |  |  |  | RW | 电池参数-功能控制位 Bit0：SOC控制禁用（0：使用SOC；1：禁用SOC） | Battery Parameters - Function Control Bits Bit0: SOC control disabled (0: use SOC; 1: disable SOC) | End-users
|  | 105A | BatConfig_Voltage_Float | U16 | 0.1 | V |  |  | RW | 电池参数-铅酸电池浮充电压 | Battery parameters - lead-acid battery float voltage
|  | 105B -- 105F | [7 empty] | 预留 | Reserved
PCC功率采集设备配置 | PCC power harvesting equipment configuration | 1060 | PCCSampleMode | U16 |  |  | 0 | 2 | RW | PCC功率采集设备配置 0：不使用 1：电表 2：CT 3：ARPC 4：采集器 | PCC power harvesting device configuration 0: not used 1: Power meter 2: CT 3: ARPC 4: Collector | End-users
谐振检测灵敏度 | Resonance detection sensitivity | 1061 | Resonance_Sensitivity | U16 |  |  | 1 | 100 | RW | 谐振检测灵敏度 | Resonance detection sensitivity | End-users
CT变比设置 | CT ratio setting | 1062 | CT_rate | U16 |  |  |  |  | RW | CT变比设置 | CT ratio setting | [7 empty] | 写入时，固定的首地址为0x1062，长度为1 | Fixed first address of 0x1062 and length 1 when writing in
硬防逆流开关 | Hard backflow prevention switch | 1063 | Hard_Reflux_Config | U16 |  |  |  |  | RW | 硬防逆流开关：0禁用/1使用 | Hard anti-backflow switch: 0 disabled / 1 used | [7 empty] | 不使用(仅对于三相储能机型) | Not used (only for 3-phase energy storage models)
干/湿接点控制 | Dry/wet contact control | 1064 | Dry_Contact | U16 |  |  | 0 | 3 | RW | 干接点控制 0：禁用干接点； 1：发电机模式； 2：继电器模式1（离网输出高，其余为低）； 3：继电器模式2（离网输出低，其余为高）； | Dry contact control 0: disable dry contact; 1: generator mode; 2: relay mode 1 (off-grid output high, rest low); 3: relay mode 2 (off-grid output low, rest high); | [7 empty] | 写入时，固定的首地址为0x1064，长度为1 | On write, fixed first address 0x1064, length 1
|  | 1065 | Wet_Contact | U16 |  |  | 0 |  | RW | 湿接点控制（预留） 0：禁用湿接点 | Wet contact control (reserved) 0: wet contact disabled | [7 empty] | 暂未使用，可读取 | Not used at the moment, readable
PV支路 | PV branch circuit | 1066 | pv_branch_current_limit | U16 | 0.1 | A | 0 | 65535 | RW | PV支路过流保护 | PV branch overcurrent protection
|  | 1067 -- 107F | [7 empty] | 预留 | Reserved
|  | 1080 -- 1083 | AddressMask_Config_Basic3 | U64 |  |  |  |  | R | 本地址开始的64个寄存器地址字的掩码区。 参看地址0x0040的说明 | Mask area for 64 register address words starting at this address. Refer to description of address 0x0040 | Installers | 00000000 | 0000000F |  |  |  |  | 用于区分哪些地址有效，哪些地址无效，主要作用就是不同机型使用的寄存器不同，通过掩码做区分。此块区域支持任意读取。 | Used to distinguish which addresses are valid and which are not. The main purpose is to distinguish between different registers used by different models by means of a mask. This area can be read at will.
电弧检测参数配置 | Arc detection parameter configuration | 1084 | ArcingAlarmEnable | U16 |  |  | 1 |  | RW | 使能电弧检测功能 | Enables arc detection function | Installers | [6 empty] | 暂未使用，可读取 | Not in use yet, readable
|  | 1085 | PeakToPeakSet | U16 | 1 |  | 0x64 |  | RW | 峰峰值设定 | Peak-to-peak setting | Installers
|  | 1086 | VarianceSet | U16 | 1 |  | 0x95 |  | RW | 方差设定 | Variance setting | Installers
|  | 1087 | HarmonicEnergySet | U16 | 1 |  | 0x01 |  | RW | 谐波能量设定 | Harmonic energy setting | Installers
|  | 1088 | AmplitudeVarianceSet | U16 | 1 |  | 0x01 |  | RW | 幅值方差设定 | Magnitude variance setting | Installers
|  | 1089 | TimeDomWeiSet | U16 | 1 |  | 0x01 |  | RW | 时域权重设定 | Time domain weighting setting | Installers
|  | 108A | FreDomWeiSet | U16 | 1 |  | 0x05 |  | RW | 频域权重设定 | Frequency weight setting | Installers
|  | 108B | ArcDetectSensitivity | U16 | 1 |  | 0x14 |  | RW | 电弧检测灵敏度 | Arc detection sensitivity | Installers
|  | 108C | ArcAlarmShutdownThreshold | U16 | 1 |  | 0x05 |  | RW | 电弧报警计数关机阀值 | Arc Alarm Count Shutdown Threshold | Installers
|  | 108D | ArcSelfCheckCommand | U16 |  |  | 0x01 |  | RW | 写 1表示开始自检（自检所有通道）。 自检结束后自动清零。 | Write 1 to start self-test (self-test all channels). Auto-zero at the end of the self-test. | Installers
|  | 108E | ArcingAlarmClear | U16 | 1 |  | 0x1234 | 0x1234 | RW | 写入 0x1234 清除电弧报警(所有通道) | Write 0x1234 Clear Arc Alarm (all channels) | Installers
|  | 108F | ArcAlarmCnt | U16 | 1 |  |  |  | RW | 电弧报警计数 | Arc alarm count
|  | 1090 | AfciResult | U16 | 1 |  |  |  | R | 握手结果 | Handshake result
|  | 1091 | SelfCheckResult | U16 |  |  |  |  | R | Bit0—通道1自检结果（0自检成功；1自检失败或没有自检） Bit1—通道2,Bit2—通道3,Bit3—通道4,Bit4—通道5,Bit5—通道6, | Bit0-Channel 1 self-test result (0 self-test success; 1 self-test failure or no self-test) Bit1-Channel 2,Bit2-Channel 3,Bit3-Channel 4,Bit4-Channel 5,Bit5-Channel 6.
|  | 1092 | SelfCheckState | U16 |  |  |  |  | R | 通道自检状态 0：没有自检 1：自检中 2：自检完成 | Channel self-test status 0: no self-test 1: Self-test in progress 2: Self-test complete
|  | 1093 -- 109F | [7 empty] | 预留 | Reserved
PLC配置 | PLC configuration | 10A0 | PLC_Enable_Setting | U16 |  |  |  |  | RW | PLC设置运行位，为0不允许，为1允许 | PLC set operation bit, for 0 not allowed, for 1 allowed | [7 empty] | 暂未使用，可读取 | Not used yet, readable
|  | 10A1 | PLC_Com_Property | U16 | NULL | NULL | 0 |  | RW | bit0-bot1:0~1对应 1/1.5 bit2~bit4:0~7对应NONE/odd/EVEN三种校验方式 bit5~bit7 0~3 对应8/9l两种数据位长度 bit8~15 0~7 对应4800/9600/19200/38400/115200 | bit0-bot1:0~1 corresponds to 1/1.5 bit2~bit4:0~7 corresponds to NONE/odd/EVEN three kinds of checksum bit5~bit7 0~3 corresponds to 8/9l two kinds of data bit length bit8~15 0~7 corresponds to 4800/9600/19200/38400/115200 | End-users
|  | 10A2 -- 10A4 | [7 empty] | 预留 | Reserved
蓝牙配置 | Bluetooth configuration | 10A5 | BLE_Enable_Setting | U16 | NULL | NULL | 0 | 1 | RW | BLE蓝牙设置运行位，为0不允许，为1允许 | BLE Bluetooth setting operation bit, 0 is not allowed, 1 is allowed | [7 empty] | 写入时，固定的首地址为0x10A5，长度为1 | Write with a fixed first address of 0x10A5 and a length of 1
|  | 10A6 | BLE_Com_Property | U16 | NULL | NULL | 0 | 65535 | RW | bit0-bot1:0~1对应 1/1.5 bit2~bit4:0~7对应NONE/odd/EVEN三种校验方式 bit5~bit7 0~1 对应8/9l两种数据位长度 bit8~15 0~7 对应4800/9600/19200/38400/115200 | bit0-bot1:0~1 corresponds to 1/1.5 bit2~bit4:0~7 corresponds to NONE/odd/EVEN three kinds of checksum bit5~bit7 0~1 corresponds to 8/9l two kinds of data bit length bit8~15 0~7 corresponds to 4800/9600/19200/38400/115200 | [7 empty] | 暂未使用，可读取 | Not used, readable
|  | 10A7 -- 10AF | [7 empty] | 预留 | Reserved
PID参数配置 | PID parameter configuration | 10B0 | PID_Auto_running_enable | U16 |  |  | 0 | 1 | RW | PID启动自动运行。 0表示禁用；1表示使能。 | PID start auto-run. 0 means disable; 1 means enable. | End-users | [6 empty] | 暂未使用，可读取 | Not used, readable
|  | 10B1 | PID_Working_Start_Time | BCD16 | 1 | Minute | 0 | 2359 | RW | PID工作开始时间(BCD码)。 例如：最小值0x0000表示00:00； 最大值0x2359表示23:59。 | PID operation start time (BCD code). For example: minimum value 0x0000 for 00:00; Maximum value 0x2359 indicates 23:59. | End-users
|  | 10B2 | PID_Working_Hours | U16 | 1 | Minute | 0 | 65535 | RW | PID工作时长。 | PID operating duration. | End-users
|  | 10B3 | PID_Working_PV_Threshold | U16 | 0.1 | V | 0 | 65535 | RW | PID启动PV值门限。 当PV电压低于门限值时才允许PID启动。 | PID start PV value threshold. PID start is only allowed when the PV voltage is below the threshold value. | End-users
|  | 10B4 | PID_Break_Restart_Delay | U16 | 1 | Minute | 0 | 65535 | RW | PID故障关闭后重启等待时间。 | Restart wait time after PID fault shutdown. | End-users
4.2Remote control(0x1100-0x12FF)
|  | 1100 -- 1103 | AddressMask_Config_Remote1 | U64 |  |  |  |  | R | 本地址开始的64个寄存器地址字的掩码区。 参看地址0x0040的说明 | Mask area for the 64 register address words starting at this address. Refer to the description of address 0x0040 | End-users | 00000000 | 0000000F |  |  |  |  | 用于区分哪些地址有效，哪些地址无效，主要作用就是不同机型使用的寄存器不同，通过掩码做区分。此块区域支持任意读取。 | It is used to distinguish which addresses are valid and which are not. The main function is that different models use different registers and are distinguished by a mask. This area supports arbitrary reads.
远程开关机 | Remote switch on/off | 1104 | Remote_On_Off_Control | U16 |  |  | 0 | 1 | RW | 远程开关机。 0x0000：关机 0x0001：开机 | Remote power on/off. 0x0000: Power off 0x0001: power on | End-users | [6 empty] | 写入时，固定的首地址为0x10A5，长度为1 | When writing, the first address is fixed at 0x10A5 and the length is 1.
功率控制 | Power control | 1105 | Power_Control | U16 |  |  |  |  | RWV | 功率控制； Bit0：有功使能位 Bit1：无功使能位 Bit2：无功模式选择位（0：Reactive_Power；1：Power_Factor） Bit3：SVG使能位 Bit4：SVG无功模式选择位（0：Fixed_Reactive_Power；1：Reactive_Power） | Power control; Bit0: active enable bit Bit1: Reactive power enable bit Bit2: Reactive mode selection bit (0: Reactive_Power; 1: Power_Factor) Bit3: SVG enable bit Bit4: SVG reactive mode selection bit (0: Fixed_Reactive_Power; 1: Reactive_Power) | End-users | [6 empty] | 写入时，固定的首地址为此范围内任意地址，长度为范围内长度 | When writing, the first address is fixed to any address within this range, and the length is the length of the range
|  | 1106 | Active_Power_Export_Limit | U16 | 0.1 | % | 0 | 1000 | RWV | 输出最大有功功率百分比 | Output maximum active power percentage | End-users
|  | 1107 | Active_Power_Import_Limit | U16 | 0.1 | % | 0 | 1000 | RWV | 输入最大有功功率百分比 | Input maximum active power percentage | End-users
|  | 1108 | Reactive_Power_Setting | I16 | 0.1 | % | -1000 | 1000 | RWV | 无功功率百分比。 注意：最大无功功率受具体机型限制。 | Percentage of reactive power. Note: The maximum reactive power is limited by the specific model. | End-users
|  | 1109 | Power_Factor_Setting | I16 | 0.01 | p.u. | -100 | 100 | RWV | 功率因数。 注意：最低功率因数受具体机型限制。 | Power Factor. Note: The minimum power factor is limited by the specific model. | End-users
|  | 110A | Active_Power_Limit_Speed | U16 | 1 | % | 1 | 65535 | RWV | 有功功率限制变化速率 | Active power limit change rate | End-users
|  | 110B | Reactive_Power_Response_Time | U16 | 0.1 | second | 0 | 65535 | RWV | 无功功率设置响应时间 | Reactive power setting response time | End-users
|  | 110C | SVG_Fixed_Reactive_Power_Setting | I16 | 0.1 | kVar | -32768 | 32767 | RWV | SVG模式下固定无功功率大小 | Fixed reactive power magnitude in SVG mode | End-users | [6 empty] | 暂未使用，可读取 | Not used, readable
|  | 110D -- 110F | [7 empty] | 预留 | Reserved
储能工作模式设置 | Energy storage operating mode setting | 1110 | Energy_Storage_Mode_Control | U16 |  |  | 0 | 4 | RW | 储能工作模式设置； 0：自发自用模式 1：分时电价模式 2：定时充放模式 3：被动模式 4：削峰模式 5：离网模式 6：发电机模式 用于更改工作模式。 | Energy storage operating mode setting; 0: Self-generation mode 1: Time-sharing tariff mode 2: Timed charging and discharging mode 3: Passive mode 4: Peak-shaving mode 5: Off-grid mode 6: Generator mode For changing the operating mode. | End-users | [6 empty] | 写入时，固定的首地址为0x1110，长度为1 | On write, the fixed first address is 0x1110 and the length is 1
定时充放 | Timed charging and discharging | 1111 | Timing_ID | U16 |  |  | 0 | 3 | RW | 定时充放-规则序号； 序号越小，优先级越高。 成功写入该寄存器后，定时充放参数将更新为所写入序号对应的参数。 | Timed charging and discharging - rule sequence number; The lower the serial number, the higher the priority. When this register is successfully written, the timed charging parameters will be updated to the parameters corresponding to the serial number written. | End-users | [6 empty] | 写入时，固定的首地址为0x1111，长度为1或者15 长度为1时，只设置模式，不设置模式的参数。 长度为15时，设置模式、设置参数以及保存参数到EEPROM | When written, the fixed first address is 0x1111 and the length is 1 or 15 With a length of 1, only the mode is set, no parameters of the mode are set. With a length of 15, the mode is set, the parameters are set and the parameters are saved to the EEPROM
|  | 1112 | Timing_On_Off_Control | U16 |  |  | 0 | 1 | RW | 定时充放-使能控制； Bit0:充电使能 Bit1：放电使能 | Timed charge/discharge-enable control; Bit0:Charge enable Bit1: Discharge enable | End-users
|  | 1113 | Timing_Charge_Start | U16 | 1 1 | 小时 分钟 | 0 0 | 23 59 | RW | 高字节。充电开始小时 低字节。充电开始分钟 | High byte. Charging start hour Low byte. Charge start minutes | End-users
|  | 1114 | Timing_Charge_End | U16 | 1 1 | 小时 分钟 | 0 0 | 23 59 | RW | 高字节。充电结束小时 低字节。充电结束分钟 | High byte. End of charge hours Low byte. End of charge minutes | End-users
|  | 1115 | Timing_Discharge_Start | U16 | 1 1 | 小时 分钟 | 0 0 | 23 59 | RW | 高字节。放电开始小时 低字节。放电开始分钟 | High byte. Discharge start hours Low byte. Discharge start minutes | End-users
|  | 1116 | Timing_Discharge_End | U16 | 1 1 | 小时 分钟 | 0 0 | 23 59 | RW | 高字节。放电结束小时 低字节。放电结束分钟 | High byte. End of discharge hours Low byte. End of discharge minutes | End-users
|  | 1117 | Timing_Power_Charge | U32 | 1 | W | 1 | 4294967296 | RW | 定时充放-充电功率 | Timed charging and discharging - charging power | End-users
|  | 1118 | [9 empty] | End-users
|  | 1119 | Timing_Power_Discharge | U32 | 1 | W | 1 | 4294967296 | RW | 定时充放-放电功率 | Timed charging and discharging - Discharge power | End-users
|  | 111A | [9 empty] | End-users
|  | 111B -- 111E | Timing_Rsvd1 -- 4 | [6 empty] | 定时充放-预留1-4（4个） | Timed charge/discharge-reserve 1-4 (4) | End-users
|  | 111F | Timing_Control | U16 |  |  | 1 | 1 | RW | 定时充放写入控制； 写入值为1时，定时充放影子寄存器中的值更新到系统定时充放配置中； 读取时，返回上次写入操作的状态： 0x0000：成功 0x0001：正在操作 0xFFFB：操作失败，控制器拒绝响应（可能控制器正忙或配置错误） 0xFFFC：操作失败，控制器无应答 0xFFFD：操作失败，当前功能被禁止 0xFFFE：操作失败，参数存储失败 0xFFFF：操作失败，输入参数有误 | Timed charge and discharge write control; on a write value of 1, the value in the timed-charge shadow register is updated to the system timed-charge configuration On a read, the status of the last write operation is returned: 0x0000: successful 0x0001: operation in progress 0xFFFB: operation failed, controller refuses to respond (possibly controller is busy or configured incorrectly) 0xFFFC: operation failed, no response from the controller 0xFFFD: operation failed, current function is disabled 0xFFFE: operation failed, parameter storage failed 0xFFFF: operation failed, wrong input parameters | End-users
分时电价 | Time share tariff | 1120 | TOU_ID | U16 |  |  | 0 | 7 | RW | 分时电价-规则序号； 序号越小，优先级越高。 成功写入该寄存器后，分时电价参数将更新为所写入序号对应的参数。 | Time-sharing tariff - rule serial number; The smaller the serial number, the higher the priority. After a successful write to this register, the time-of-use tariff parameter will be updated to the parameter corresponding to the serial number written. | End-users | [6 empty] | 写入时，固定的首地址为0x1120，长度为1或者16 长度为1时，只设置模式，不设置模式的参数。 长度为16时，设置模式、设置参数以及保存参数到EEPROM | When written, the fixed first address is 0x1120 and the length is 1 or 16 With a length of 1, only the mode is set, no parameters of the mode are set. With a length of 16, the mode is set, the parameters are set and the parameters are saved to the EEPROM
|  | 1121 | TOU_On_Off_Control | U16 |  |  | 0 | 1 | RW | 分时电价-规则使能； 0：禁用 1：使能 | Time-sharing tariff-rule enable; 0: disabled 1: enable | End-users
|  | 1122 | TOU_Charge_Start | U16 | 1 1 | 小时 分钟 | 0 0 | 23 59 | RW | 高字节。充电开始小时 低字节。充电开始分钟 | High byte. Charging start hour Low byte. Charge start minutes | End-users
|  | 1123 | TOU_Charge_End | U16 | 1 1 | 小时 分钟 | 0 0 | 23 59 | RW | 高字节。充电结束小时 低字节。充电结束分钟 | High byte. End of charge hours Low byte. Charge end minutes | End-users
|  | 1124 | TOU_Charge_Target_SOC | U16 | 1 | % | 30 | 100 | RW | 分时电价-强制充电截止SOC； 剩余电量百分比，当电池当前SOC达到该寄存器值时，强制充电结束并进入自发自用模式，同时禁止放电。 | Timeshare-Forced charge cut-off SOC; The percentage of power remaining, when the battery's current SOC reaches this register value, the forced charge ends and enters self-generating mode, while discharging is disabled. | End-users
|  | 1125 | TOU_Charge_Power | U32 | 1 | W | 1 | 4294967296 | RW | 分时电价-强制充电功率； 设置值不能超过机器额定功率。 | Time-of-charge tariff - forced charging power; The set value must not exceed the machine's rated power. | End-users
|  | 1126 | [9 empty] | End-users
|  | 1127 | TOU_Executed_Date_Start | U16 | 1 1 | 月 日 | 1 1 | 12 31 | RW | 高字节。规则开始生效月份 低字节。规则开始生效日期 | High Byte. Month in which the rule comes into effect Low byte. Date when the rule became effective | End-users
|  | 1128 | TOU_Executed_Date_End | U16 | 1 1 | 月 日 | 1 1 | 12 31 | RW | 高字节。规则停止生效月份 低字节。规则停止生效日期 | High byte. Month the rule ceased to be in effect Low byte. The date the rule ceased to be effective | End-users
|  | 1129 | TOU_Executed_Day_of_Week | U16 |  |  |  |  | RW | 分时电价-规则生效星期； 该寄存器以位域表示，位为0表示无效星期，位为1表示有效星期 Bit0：星期一 Bit1：星期二 Bit2：星期三 Bit3：星期四 Bit4：星期五 Bit5：星期六 Bit6：星期日 | Timeshift Tariff - Week in which the rule takes effect; This register is represented as a bit field, with a bit 0 indicating an invalid week and a bit 1 indicating a valid week Bit0: Monday Bit1: Tuesday Bit2: Wednesday Bit3: Thursday Bit4: Friday Bit5: Saturday Bit6: Sunday | End-users
|  | 112A -- 112E | TOU_Rsvd1 -- 5 | [6 empty] | 分时电价-预留1-5 | Timesharing tariff - reserved 1-5 | End-users
|  | 112F | TOU_Control | U16 |  |  | 1 | 1 | RW | 分时电价-写入控制； 写入值为1时，分时电价影子寄存器中的值更新到系统分时电价配置中； 读取时，返回上次写入操作的状态： 0x0000：成功 0x0001：正在操作 0xFFFB：操作失败，控制器拒绝响应（可能控制器正忙或配置错误） 0xFFFC：操作失败，控制器无应答 0xFFFD：操作失败，当前功能被禁止 0xFFFE：操作失败，参数存储失败 0xFFFF：操作失败，输入参数有误 | Time-of-day tariff - write control; On a write value of 1, the value in the timesharing tariff shadow register is updated to the system timesharing tariff configuration; On a read, the status of the last write operation is returned: 0x0000: successful 0x0001: operation in progress 0xFFFB: operation failed, controller refused to respond (possibly controller is busy or misconfigured) 0xFFFC: operation failed, no response from the controller 0xFFFD: operation failed, current function is disabled 0xFFFE: operation failed, parameter storage failed 0xFFFF: operation failed, wrong input parameters | End-users
削峰模式 | Peak-shaving mode | 1130 -- 1131 | Peak_Shaving_Discharge_Threshold | U32 | 1 | W | 100 |  | RW | 允许系统从电网买电的功率上限 | Upper limit of the power allowed to the system to buy power from the grid | End-users | [6 empty] | 此参数为削峰模式的参数设置。 写入时，固定的首地址为0x1130，长度为4 | This parameter is the parameter setting for the peak shaving mode. When writing in, the fixed first address is 0x1130 and the length is 4
|  | 1132 -- 1133 | Peak_Shaving_Charge_Threshold | U32 | 1 | W | 100 |  | RW | 允许系统向电网卖电的功率上限 | Upper limit of the power allowed to the system to sell electricity to the grid | End-users
|  | 1134 -- 113F | [7 empty] | 预留 | Reserved
|  | 1140 -- 1143 | AddressMask_Config_Remote2 | U64 |  |  |  |  | R | 本地址开始的64个寄存器地址字的掩码区。 参看地址0x0040的说明 | Mask area for the 64 register address words starting at this address. Refer to the description of address 0x0040 | End-users | 00000000 | 0000000F |  |  |  |  | 用于区分哪些地址有效，哪些地址无效，主要作用就是不同机型使用的寄存器不同，通过掩码做区分。此块区域支持任意读取。 | Used to distinguish which addresses are valid and which are not. The main function is that different models use different registers and make the distinction by masking them. This area supports arbitrary reads.
离网模式 | Off-grid mode | 1144 | Off_Grid_Charge_Source | U16 |  |  | 0 | 2 | RW | 离网模式 - 充电源选择： 0：电网 1：发电机 2：预留 | Off-grid mode - Charging source selection: 0: Grid 1: Generator 2: Reserved | [7 empty] | 写入时，固定的首地址为0x1144，长度为3 此处有个特殊情况，可以单独从首地址为0x1146写入长度为1的数据 | When writing, the first address is fixed at 0x1144 and the length is 3 There is a special case where data of length 1 can be written from a separate first address of 0x1146
|  | 1145 | Off_Grid_Grid_Power | U16 | 0.01 | kW | 0 | 65535 | RW | 离网模式 - 电网取电功率 | Off-grid mode - Grid draw power
|  | 1146 | Off_Grid_DG_Power | U16 | 0.01 | kW | 0 | 65535 | RW | 离网模式 - 发电机最大取电功率 | Off-grid mode - maximum generator power draw
|  | 1147 -- 117F | [7 empty] | 预留 | Reserved
|  | 1180 -- 1183 | AddressMask_Config_Remote3 | U64 |  |  |  |  | R | 本地址开始的64个寄存器地址字的掩码区。 参看地址0x0040的说明 | Mask area for the 64 register address words starting at this address. Refer to the description of address 0x0040 | End-users | 00000000 | 0000000F |  |  |  |  | 用于区分哪些地址有效，哪些地址无效，主要作用就是不同机型使用的寄存器不同，通过掩码做区分。此块区域支持任意读取。 | It is used to distinguish which addresses are valid and which are not. The main function is that different models use different registers and the distinction is made by means of a mask. This area can be read at will.
被动模式 | Passive mode | 1184 | Passive_Timeout | U16 | 1 | 秒 | 0 | 65535 | RW | 被动模式-超时控制； 默认值：0； 设置被动模式通信超时时间，当逆变器在超过该寄存器所设置时间内没有接收到任何通讯，逆变器强制执行超时动作。 特殊的，向该寄存器写入0将禁用超时功能。 | Passive mode - timeout control; Default value: 0; Sets the passive mode communication timeout time. When the inverter does not receive any communication for longer than the time set in this register, the inverter forces a timeout action. Specially, writing 0 to this register will disable the timeout function. | End-users | [6 empty] | 写入时，固定的首地址为0x1184，长度为2 | When writing, the first address is fixed at 0x1184 and the length is 2.
|  | 1185 | Passive_Timeout_Action | U16 |  |  | 0 | 1 | RW | 被动模式-超时动作； 0：强制待机 1：强制恢复为进入被动模式前的储能模式 | Passive mode - timeout action; 0: forces standby 1: forced return to the energy storage mode before entering the passive mode | End-users
|  | 1186 | Passive_Rsvd1 | [6 empty] | 被动模式-预留1 | Passive Mode-Reserve 1 | End-users
Manual模式 | Manual mode | 1187 | Passive_Manual_Gdes | I32 | 1 | W | -2147483648 | 2147483647 | RW | Manual模式期望电网功率（Gdes）； 正值表示功率方向“从电网至系统”； 负值表示功率方向“从系统至电网”。 | Manual mode desired grid power (Gdes); Positive values indicate the power direction from grid to system";Negative values indicate the power direction "from the system to the grid"." | End-users | [6 empty] | 写入时，固定的首地址为0x1187，长度为6 此处有个特殊情况，可以单独从首地址为0x1189写入长度为4的数据 | When writing, the fixed first address is 0x1187 and the length is 6 There is a special case here where data of length 4 can be written from a separate first address of 0x1189
|  | 1188 | [9 empty] | End-users
|  | 1189 | Passive_Manual_Blo | I32 | 1 | W | -2147483648 | 2147483647 | RW | Manual模式电池最低充放电功率（Blo）； 正值表示充电； 负值表示放电。 | Manual mode battery minimum charge and discharge power (Blo); Positive values indicate charging; Negative values indicate discharging. | End-users
|  | 118A | [9 empty] | End-users
|  | 118B | Passive_Manual_Bup | I32 | 1 | W | -2147483648 | 2147483647 | RW | Manual模式电池最高充放电功率（Bup）； 正值表示充电； 负值表示放电。 | Maximum charge/discharge power (Bup) for Manual mode batteries; Positive values indicate charging; Negative values indicate discharging. | End-users
|  | 118C | [9 empty] | End-users
|  | 118D | Passive_Manual_Gdzup | I32 | 1 | W | -2147483648 | 2147483647 | RW | Manual模式允许卖电功率(Gdzup)； 正值表示功率方向“从电网至系统”； 负值表示功率方向“从系统至电网”。 | Manual mode permissible power selling (Gdzup); Positive values indicate the power direction from grid to system";Negative values indicate the power direction "from the system to the grid"." | End-users | [6 empty] | 参数暂时未用到，可以读取，但不可写入 | The parameter is not used at the moment and can be read, but not written "
|  | 118E | [9 empty] | End-users
|  | 118F | Passive_Manual_Gdzlo | I32 | 1 | W | -2147483648 | 2147483647 | RW | Manual模式允许买电功率(Gdzlo)； 正值表示功率方向“从电网至系统”； 负值表示功率方向“从系统至电网”。 | Manual mode allows the purchase of power (Gdzlo); Positive values indicate the power direction from the grid to the system"; | End-users
|  | 1190 | [9 empty] | End-users
Scheduler模式 | Scheduler mode | 1191 | Passive_Scheduler_Gdes_Ante | I32 | 1 | W | -2147483648 | 2147483647 | RW | Scheduler模式期望电网功率(Gdes_Ante)； 计划任务参数，计划时间段内有效。 正值表示功率方向“从电网至系统”； 负值表示功率方向“从系统至电网”。 | Scheduler mode expected grid power (Gdes_Ante); Scheduled task parameter, valid for the scheduled time period. Positive values indicate the power direction from grid to system"; | End-users
|  | 1192 | [9 empty] | End-users
|  | 1193 | Passive_Scheduler_Blo_Ante | I32 | 1 | W | -2147483648 | 2147483647 | RW | Scheduler模式电池最低充放电功率（Blo_Ante）； 计划任务参数，计划时间段内有效。 正值表示功率方向“从电网至系统”； 负值表示功率方向“从系统至电网”。 | Scheduler mode battery minimum charge/discharge power (Blo_Ante); Scheduled task parameter, valid for the scheduled time period. Positive values indicate the power direction from grid to system"; | End-users
|  | 1194 | [9 empty] | End-users
|  | 1195 | Passive_Scheduler_Bup_Ante | I32 | 1 | W | -2147483648 | 2147483647 | RW | Scheduler模式电池最高充放电功率（Bup_Ante）； 计划任务参数，计划时间段内有效。 正值表示功率方向“从电网至系统”； 负值表示功率方向“从系统至电网”。 | Scheduler mode battery maximum charge/discharge power (Bup_Ante); Scheduled task parameter, valid for the scheduled time period. Positive values indicate the power direction from grid to system"; | End-users
|  | 1196 | [9 empty] | End-users
|  | 1197 | Passive_Scheduler_Gdzup_Ante | I32 | 1 | W | -2147483648 | 2147483647 | RW | Scheduler模式允许卖电功率(Gdzup_Ante)； 计划任务参数，计划时间段内有效。 正值表示功率方向“从电网至系统”； 负值表示功率方向“从系统至电网”。 | Scheduler mode allows the sale of electrical power (Gdzup_Ante); Scheduled task parameter, valid for the scheduled time period. Positive values indicate the power direction from grid to system"; | End-users
|  | 1198 | [9 empty] | End-users
|  | 1199 | Passive_Scheduler_Gdzlo_Ante | I32 | 1 | W | -2147483648 | 2147483647 | RW | Scheduler模式允许买电功率(Gdzlo_Ante)； 计划任务参数，计划时间段内有效。 正值表示功率方向“从电网至系统”； 负值表示功率方向“从系统至电网”。 | Scheduler mode allows the purchase of electrical power (Gdzlo_Ante); Scheduled task parameter, valid for the scheduled time period. Positive values indicate the power direction from grid to system"; | End-users
|  | 119A | [9 empty] | End-users
|  | 119B | Passive_Scheduler_Gdes_Post | I32 | 1 | W | -2147483648 | 2147483647 | RW | Scheduler模式期望电网功率(Gdes_Post)； 计划任务参数，计划时间段后有效。 正值表示功率方向“从电网至系统”； 负值表示功率方向“从系统至电网”。 | Scheduler mode expected grid power (Gdes_Post); Scheduled task parameter, valid after the scheduled time period. Positive values indicate the power direction from grid to system"; | End-users
|  | 119C | [9 empty] | End-users
|  | 119D | Passive_Scheduler_Blo_Post | I32 | 1 | W | -2147483648 | 2147483647 | RW | Scheduler模式电池最低充放电功率（Blo_Post）； 计划任务参数，计划时间段后有效。 正值表示功率方向“从电网至系统”； 负值表示功率方向“从系统至电网”。 | Scheduler mode battery minimum charge/discharge power (Blo_Post); Scheduled task parameter, valid after the scheduled time period. Positive values indicate the power direction from grid to system"; | End-users
|  | 119E | [9 empty] | End-users
|  | 119F | Passive_Scheduler_Bup_Post | I32 | 1 | W | -2147483648 | 2147483647 | RW | Scheduler模式电池最高充放电功率（Bup_Post）； 计划任务参数，计划时间段后有效。 正值表示功率方向“从电网至系统”； 负值表示功率方向“从系统至电网”。 | Scheduler mode battery maximum charge/discharge power (Bup_Post); Scheduled task parameter, valid after the scheduled time period. Positive values indicate the power direction from grid to system"; | End-users
|  | 11A0 | [9 empty] | End-users
|  | 11A1 | Passive_Scheduler_Gdzup_Post | I32 | 1 | W | -2147483648 | 2147483647 | RW | Scheduler模式允许卖电功率(Gdzup_Post)； 计划任务参数，计划时间段后有效。 正值表示功率方向“从电网至系统”； 负值表示功率方向“从系统至电网”。 | Scheduler mode allows selling power (Gdzup_Post); Scheduled task parameter, valid after the scheduled time period. Positive values indicate the power direction from grid to system"; | End-users
|  | 11A2 | [9 empty] | End-users
|  | 11A3 | Passive_Scheduler_Gdzlo_Post | I32 | 1 | W | -2147483648 | 2147483647 | RW | Scheduler模式允许买电功率(Gdzlo_Post)； 计划任务参数，计划时间段后有效。 正值表示功率方向“从电网至系统”； 负值表示功率方向“从系统至电网”。 | Scheduler mode allows buying power (Gdzlo_Post); Scheduled task parameter, valid after the scheduled time period. Positive values indicate the power direction from grid to system"; | End-users
|  | 11A4 | [9 empty] | End-users
|  | 11A5 | Passive_Scheduler_StartTime | U32 | 1 | 秒 | 0 | 4294967296 | RW | Scheduler模式应用期望参数设定值的开始时间； StartTime为unix时间格式，由于系统内部时间默认为格林威治时间（GMT）,因此在设置此参数时，应注意所在国当地时区，StartTime=（当地Unix Time）±（当地时间与UTC/GMT的时差对应的秒数） | The start time at which the Scheduler mode applies the value set for the desired parameter; StartTime is in unix time format, since the system internal time defaults to Greenwich Mean Time (GMT),when setting this parameter, you should pay attention to the local time zone of your country, StartTime=(local Unix Time) ± (the number of seconds corresponding to the time difference between local time and UTC/GMT) | End-users
|  | 11A6 | [9 empty] | End-users
|  | 11A7 | Passive_Scheduler_DurationTime | U32 | 1 | 秒 | 0 | 4294967296 | RW | Scheduler模式应用期望参数设定值的持续时间(DurationTime) | DurationTime for the Scheduler mode to apply the desired parameter settings | End-users
|  | 11A8 | [9 empty] | End-users
|  | 11A9 | Passive_Scheduler_ManagementMode | U16 |  |  | 0 | 2 | RW | Scheduler模式管理模式选择(ManagementMode)； 0：自发自用模式 1：Manual模式 2：Scheduler模式 只能输入0、1、2，其他数据无效。 | Scheduler mode management mode selection (ManagementMode); 0: Spontaneous mode 1: Manual mode 2: Scheduler mode Only 0, 1 and 2 can be entered, other data is invalid. | End-users
|  | 11AA -- 11BF | [7 empty] | 预留 | Reserved
|  | 11C0 -- 11C3 | AddressMask_Config_Remote4 | U64 |  |  |  |  | R | 本地址开始的64个寄存器地址字的掩码区。 参看地址0x0040的说明 | Mask area for the 64 register address words starting at this address. Refer to the description of address 0x0040 | End-users | 00000000 | 0000000F |  |  |  |  | 用于区分哪些地址有效，哪些地址无效，主要作用就是不同机型使用的寄存器不同，通过掩码做区分。此块区域支持任意读取。 | It is used to distinguish which addresses are valid and which are not. The main function is that different models use different registers and are distinguished by a mask. This area can be read at will.
电站通讯中断保护功能 | Power station communication interruption protection | 11C4 | CommBreak_Protect_Enable | U16 | 1 |  | 0 | 65535 | RW | 电站通讯中断保护功能使能寄存器： 0：电站通讯中断保护功能失能（默认） 1：电站通讯中断保护功能使能 | Power station communication interrupt protection function enable register: 0: Power station communication interrupt protection function disable (default) 1: Power station communication interruption protection function enabled | [7 empty] | 参数暂时未用到 | Parameters not used at the moment
|  | 11C5 | CommBreak_Recovery_Mode | U16 | 1 |  | 0 | 65535 | RW | 电站通讯中断保护恢复方式： 0：自动恢复（默认） 1：手动恢复 | Power station communication interruption protection recovery method: 0: automatic recovery (default) 1: Manual recovery
|  | 11C6 | CommBreak_Threshold_Time | U16 | 1 | min | 10 | 120 | RW | 电站通讯中断阈值时间： 10-120min（默认:15min） | Power station communication interruption threshold time: 10-120min (default:15min)
|  | 11C7 | CommBreak_Mode_Judge | U16 | 1 |  | 0 | 65535 | RW | 电站通讯中断数据监测源： 0：485（默认） 1：WIFI 3：PLC | Power station communication interruption data monitoring source: 0: 485 (default) 1: WIFI 3: PLC
|  | 11C8 | CommBreak_Alarm_Clear | U16 | 1 |  | 0 | 65535 | W | 电站通讯中断报警清除寄存器： 写入“1”值表示清除通讯中断报警状态 | Power station communication interruption alarm clear register: Write a value of 1" to clear the communication interruption alarm status"
4.3Inverter returns read-only results(0x1300-0x15FF)
|  | 1300 -- 1303 | AddressMask_Config_ReadOnly_Result1 | U64 |  |  |  |  | R | 本地址开始的64个寄存器地址字的掩码区。 参看地址0x0040的说明 | Mask area for the 64 register address words starting at this address. Refer to the description of address 0x0040 |  | 00000000 | 0000000F |  |  |  |  | 用于区分哪些地址有效，哪些地址无效，主要作用就是不同机型使用的寄存器不同，通过掩码做区分。此块区域只支持读取掩码，如果读取其他区域的数据，会导致函数参数异常而死机。 | It is used to distinguish which addresses are valid and which are not. The main function is that different models use different registers and are distinguished by a mask. This area only supports reading masks, if you read data from other areas, it will cause the function parameters to be abnormal and the machine will die.
意大利自动测试 | Automatic testing in Italy | 1304 | Italay_Autotest_Result1 | U16 | 0.1 | V |  |  | R | 意大利自动测试59.s1。 默认设定一级过压保护值。 | Italian Auto Test 59.s1. Default setting of one level of overvoltage protection value. | [7 empty] | 暂未使用，不可读取 | Not in use, not readable
|  | 1305 | Italay_Autotest_Result2 | U16 | 1 | ms |  |  | R | 意大利自动测试59.s1。 默认设定一级过压保护时间。 | Italy Auto Test 59.s1. Default setting of the first level overvoltage protection time.
|  | 1306 | Italay_Autotest_Result3 | U16 | 0.1 | V |  |  | R | 意大利自动测试59.s1。 一级过压保护值测试结果。 | Italian automatic test 59.s1. Test result for the first level overvoltage protection value.
|  | 1307 | Italay_Autotest_Result4 | U16 | 1 | ms |  |  | R | 意大利自动测试59.s1。 一级过压保护时间测试结果。 | Italy Auto Test 59.s1. Level 1 overvoltage protection time test result.
|  | 1308 | Italay_Autotest_Result5 | U16 | 0.1 | V |  |  | R | 意大利自动测试59.s2。 默认设定二级过压保护值。 | Italy Auto Test 59.s2. Default setting of the second level overvoltage protection value.
|  | 1309 | Italay_Autotest_Result6 | U16 | 1 | ms |  |  | R | 意大利自动测试59.s2。 默认设定二级过压保护时间。 | Italy Auto Test 59.s2. Default setting for secondary overvoltage protection time.
|  | 130A | Italay_Autotest_Result7 | U16 | 0.1 | V |  |  | R | 意大利自动测试59.s2。 二级过压保护值测试结果。 | Italy Auto Test 59.s2. Test result for secondary overvoltage protection value.
|  | 130B | Italay_Autotest_Result8 | U16 | 1 | ms |  |  | R | 意大利自动测试59.s2。 二级过压保护时间测试结果。 | Italy Auto Test 59.s2. Secondary overvoltage protection time test result.
|  | 130C | Italay_Autotest_Result9 | U16 | 0.1 | V |  |  | R | 意大利自动测试27.s1。 默认设定一级欠压保护值。 | Italian automatic test 27.s1. Default setting of the primary undervoltage protection value.
|  | 130D | Italay_Autotest_Result10 | U16 | 1 | ms |  |  | R | 意大利自动测试27.s1。 默认设定一级欠压保护时间。 | Italy Auto Test 27.s1. Default setting of primary undervoltage protection time.
|  | 130E | Italay_Autotest_Result11 | U16 | 0.1 | V |  |  | R | 意大利自动测试27.s1。 一级欠压保护值测试结果。 | Italy Auto Test 27.s1. Test result for level 1 undervoltage protection value.
|  | 130F | Italay_Autotest_Result12 | U16 | 1 | ms |  |  | R | 意大利自动测试27.s1。 一级欠压保护时间测试结果。 | Italy Auto Test 27.s1. Level 1 undervoltage protection time test result.
|  | 1310 | Italay_Autotest_Result13 | U16 | 0.1 | V |  |  | R | 意大利自动测试27.s2。 默认设定二级欠压保护值。 | Italy Auto Test 27.s2. Default setting of the second level undervoltage protection value.
|  | 1311 | Italay_Autotest_Result14 | U16 | 1 | ms |  |  | R | 意大利自动测试27.s2。 默认设定二级欠压保护时间。 | Italy Auto Test 27.s2. Default setting for secondary undervoltage protection time.
|  | 1312 | Italay_Autotest_Result15 | U16 | 0.1 | V |  |  | R | 意大利自动测试27.s2。 二级欠压保护值测试结果。 | Italian automatic test 27.s2. Test result for secondary undervoltage protection value.
|  | 1313 | Italay_Autotest_Result16 | U16 | 1 | ms |  |  | R | 意大利自动测试27.s2。 二级欠压保护时间测试结果。 | Italy Auto Test 27.s2. Secondary undervoltage protection time test result.
|  | 1314 | Italay_Autotest_Result17 | U16 | 0.01 | Hz |  |  | R | 意大利自动测试81>s1。 默认设定一级过频保护值。 | Italian automatic test 81>s1. Default setting for level 1 underfrequency protection value.
|  | 1315 | Italay_Autotest_Result18 | U16 | 1 | ms |  |  | R | 意大利自动测试81>s1。 默认设定一级过频保护时间。 | Italian automatic test 81>s1. Default setting of primary overfrequency protection time.
|  | 1316 | Italay_Autotest_Result19 | U16 | 0.01 | Hz |  |  | R | 意大利自动测试81>s1。 一级过频保护值测试结果。 | Italian automatic test 81>s1. Test result for the first level of overfrequency protection value.
|  | 1317 | Italay_Autotest_Result20 | U16 | 1 | ms |  |  | R | 意大利自动测试81>s1。 一级过频保护时间测试结果。 | Italian Auto Test 81>s1. Level 1 overfrequency protection time test result.
|  | 1318 | Italay_Autotest_Result21 | U16 | 0.01 | Hz |  |  | R | 意大利自动测试81>s2。 默认设定二级过频保护值。 | Italian Auto Test 81>s2. Default setting of the second level overfrequency protection value.
|  | 1319 | Italay_Autotest_Result22 | U16 | 1 | ms |  |  | R | 意大利自动测试81>s2。 默认设定二级过频保护时间。 | Italian Auto Test 81>s2. Default setting for secondary overfrequency protection time.
|  | 131A | Italay_Autotest_Result23 | U16 | 0.01 | Hz |  |  | R | 意大利自动测试81>s2。 二级过频保护值测试结果。 | Italy Auto Test 81>s2. Test result for secondary overfrequency protection value.
|  | 131B | Italay_Autotest_Result24 | U16 | 1 | ms |  |  | R | 意大利自动测试81>s2。 二级过频保护时间测试结果。 | Italian Auto Test 81>s2. Secondary overfrequency protection time test result.
|  | 131C | Italay_Autotest_Result25 | U16 | 0.01 | Hz |  |  | R | 意大利自动测试81<s1。 默认设定一级欠频保护值。 | Italian Auto Test 81<s1. Default setting of the first level underfrequency protection value.
|  | 131D | Italay_Autotest_Result26 | U16 | 1 | ms |  |  | R | 意大利自动测试81<s1。 默认设定一级欠频保护时间。 | Italian Auto Test 81<s1. Default setting of primary underfrequency protection time.
|  | 131E | Italay_Autotest_Result27 | U16 | 0.01 | Hz |  |  | R | 意大利自动测试81<s1。 一级欠频保护值测试结果。 | Italy Auto Test 81<s1. Level 1 underfrequency protection value test result.
|  | 131F | Italay_Autotest_Result28 | U16 | 1 | ms |  |  | R | 意大利自动测试81<s1。 一级欠频保护时间测试结果。 | Italy Auto Test 81<s1. Level 1 underfrequency protection time test result.
|  | 1320 | Italay_Autotest_Result29 | U16 | 0.01 | Hz |  |  | R | 意大利自动测试81<s2。 默认设定二级欠频保护值。 | Italian Auto Test 81<s2. Default setting of the second level underfrequency protection value.
|  | 1321 | Italay_Autotest_Result30 | U16 | 1 | ms |  |  | R | 意大利自动测试81<s2。 默认设定二级欠频保护时间。 | Italy Auto Test 81<s2. Default setting for secondary underfrequency protection time.
|  | 1322 | Italay_Autotest_Result31 | U16 | 0.01 | Hz |  |  | R | 意大利自动测试81<s2。 二级欠频保护值测试结果。 | Italy Auto Test 81<s2. Test result for secondary underfrequency protection value.
|  | 1323 | Italay_Autotest_Result32 | U16 | 1 | ms |  |  | R | 意大利自动测试81<s2。 二级欠频保护时间测试结果。 | Italian automatic test 81<s2. Secondary underfrequency protection time test results.
|  | 1324 -- 1333 | Italay_Autotest_Result33 -- 48 | [6 empty] | 意大利自动测试结果33-48（16个） | Italian automatic test results 33-48 (16)
|  | 1334-133F | [7 empty] | 预留 | Reserved
|  | 1340 -- 1343 | AddressMask_Config_ReadOnly_Result2 | U64 |  |  |  |  | R | 本地址开始的64个寄存器地址字的掩码区。 参看地址0x0040的说明 | Mask area for the 64 register address words starting at this address. Refer to the description of address 0x0040 |  | 00000000 | 0000000F |  |  |  |  | 此块区域只支持固定首地址读取一块区域的数据 | This block only supports reading data from one block with a fixed first address
IV曲线扫描 | IV curve scanning | 1344 -- 137E | IVCurve_Voltage1 -- 30 | U16 | 0.1 | V |  |  | R | IV曲线扫描电压1-30。 | IV curve scan voltage 1-30. | [7 empty] | 间隔2个地址 | 2 addresses apart
|  | 1345 -- 137F | IVCurve_Current1 -- 30 | U16 | 0.01 | A |  |  | R | IV曲线扫描电流1-30。 | IV curve scan current 1-30. | [7 empty] | 间隔2个地址 | 2 addresses apart
|  | 1380 -- 1383 | AddressMask_Config_ReadOnly_Result3 | U64 |  |  |  |  | R | 本地址开始的64个寄存器地址字的掩码区。 参看地址0x0040的说明 | Mask area for 64 register address words starting at this address. Refer to the description of address 0x0040 |  | 00000000 | 0000000F |  |  |  |  | 此块区域只支持固定首地址读取一块区域的数据 | This area only supports reading data from one area with a fixed first address
IV曲线扫描 | IV curve scanning | 1384 -- 13BE | IVCurve_Voltage31 -- 60 | U16 | 0.1 | V |  |  | R | IV曲线扫描电压31-60。 | IV curve scan voltage 31-60. | [7 empty] | 间隔2个地址 | 2 addresses apart
|  | 1385 -- 13BF | IVCurve_Current31 -- 60 | U16 | 0.01 | A |  |  | R | IV曲线扫描电流31-60。 | IV curve scan current 31-60. | [7 empty] | 间隔2个地址 | 2 addresses apart
|  | 13C0 -- 13C3 | AddressMask_Config_ReadOnly_Result4 | U64 |  |  |  |  | R | 本地址开始的64个寄存器地址字的掩码区。 参看地址0x0040的说明 | Mask area for 64 register address words starting at this address. Refer to the description of address 0x0040 |  | 00000000 | 0000000F |  |  |  |  | 此块区域只支持固定首地址读取一块区域的数据 | This area only supports reading data from one area with a fixed first address
IV曲线扫描 | IV curve scan | 13C4 -- 13FE | IVCurve_Voltage61 -- 90 | U16 | 0.1 | V |  |  | R | IV曲线扫描电压61-90。 | IV curve scan voltage 61-90. | [7 empty] | 间隔2个地址 | 2 addresses apart
|  | 13C5 -- 13FF | IVCurve_Current61 -- 90 | U16 | 0.01 | A |  |  | R | IV曲线扫描电流61-90。 | IV curve scan current 61-90. | [7 empty] | 间隔2个地址 | 2 addresses apart
|  | 1400 --1403 | AddressMask_Config_ReadOnly_Result5 | U64 |  |  |  |  | R | 本地址开始的64个寄存器地址字的掩码区。 参看地址0x0040的说明 | Mask area for 64 register address words starting at this address. Refer to the description of address 0x0040 |  | 00000000 | 0000000F |  |  |  |  | 此块区域只支持固定首地址读取一块区域的数据 | This area only supports reading data from one area with a fixed first address
IV曲线扫描 | IV curve scan | 1404 -- 143E | IVCurve_Voltage91 -- 120 | U16 | 0.1 | V |  |  | R | IV曲线扫描电压91-120。 | IV curve scan voltage 91-120. | [7 empty] | 间隔2个地址 | 2 addresses apart
|  | 1405 -- 143F | IVCurve_Current91 -- 120 | U16 | 0.01 | A |  |  | R | IV曲线扫描电流91-120。 | IV curve scan current 91-120. | [7 empty] | 间隔2个地址 | 2 addresses apart
|  | 1440 -- 1443 | AddressMask_Config_ReadOnly_Result6 | U64 |  |  |  |  | R | 本地址开始的64个寄存器地址字的掩码区。 参看地址0x0040的说明 | Mask area for 64 register address words starting at this address. Refer to the description of address 0x0040 |  | 00000000 | 0000000F |  |  |  |  | 此块区域只支持固定首地址读取一块区域的数据 | This area only supports reading data from one area with a fixed first address
IV曲线扫描 | IV curve scan | 1444 -- 147E | IVCurve_Voltage121 -- 150 | U16 | 0.1 | V |  |  | R | IV曲线扫描电压121-150。 | IV curve scan voltage 121-150. | [7 empty] | 间隔2个地址 | 2 addresses apart
|  | 1445 -- 147F | IVCurve_Current121 -- 150 | U16 | 0.01 | A |  |  | R | IV曲线扫描电流121-150。 | IV curve scan current 121-150. | [7 empty] | 间隔2个地址 | 2 addresses apart
历史事件 | Historical events | 1480 -- 160C | HistoryEventList_ID1 -- 100 | U16 |  |  |  |  | R | 历史事件ID最近第1-100条（100个）。 | History Event ID 1st-100th most recent (of 100). | [7 empty] | 每个ID间隔4个地址 读取时，这几个数据构成第1条历史故障信息的ID以及触发时间。范围内单个读取始终会读到事件ID，只有四个寄存器一起读取才能读到完整的数据。 最多一次读取10条历史数据 | Each ID is spaced 4 addresses apart When read, these form the ID of the 1st historical fault message as well as the trigger time. Individual reads within the range will always read the event ID, only four registers read together will read the complete data. Up to 10 historical reads at a time
|  | 1481 -- 160D | HistoryEventList_yM1 -- 100 | U16 |  |  |  |  | R | 历史事件时间最近第1-100条（100个）。 高字节：年份十进制数低两位； 低字节：月份。 | History event time 1st-100th most recent (100). High byte: year decimal lower two digits; Low byte: month.
|  | 1482 -- 160E | HistoryEventList_dH1 -- 100 | U16 |  |  |  |  | R | 历史事件时间最近第1-100条（100个）。 高字节：日期； 低字节：小时。 | Historical event time most recent 1-100th entry (of 100). High byte: date; Low byte: hour.
|  | 1483 -- 160F | HistoryEventList_ms1 -- 100 | U16 |  |  |  |  | R | 历史事件时间最近第1-100条（100个）。 高字节：分钟； 低字节：秒。 | Historical event time most recent 1-100th (of 100). High byte: minutes; Low byte: seconds.
历史电能 | Historical electricity | 1610 -- 165E | EnergyStatistics1 -- 40 | U32 | 0.01 | kWh |  |  | R | 历史电能统计数据第1-40条（40个）。U32每次间隔2个地址。 对应日期时间参考电能统计回传设置寄存器。 | Historical power statistics 1st-40th (of 40). u32 2 addresses per interval. Corresponding date and time reference to power statistics return setting register. | [7 empty] | 此块区域的读取与地址0x1030到0x1033的设置有关，显示的都是电量数据，读取之前需要先设置0x1030到0x1033的值。 如果是年，那么前12条数据就代表12个月的电量数据。 如果是月，那么前31条数据就代表31天的电量数据。 | The reading of this area is related to the setting of addresses 0x1030 to 0x1033, which show all the power data, and the values 0x1030 to 0x1033 need to be set before reading.If it is a year, then the first 12 bars represent 12 months of power data.If it is a month, then the first 31 bars of data represent 31 days of power data."
1611 -- 165F
4.4Core function configuration(0x2000-0x207F)
|  | 2000 -- 2003 | AddressMask_Config_Core1 | U64 |  |  |  |  | R | 本地址开始的64个寄存器地址字的掩码区。 参看地址0x0040的说明 | Mask area for the 64 register address words starting at this address. Refer to the description of address 0x0040 |  | 00000000 | 0000000F |  |  |  |  | 用于区分哪些地址有效，哪些地址无效，主要作用就是不同机型使用的寄存器不同，通过掩码做区分。此块区域支持任意读取。 | It is used to distinguish which addresses are valid and which are not. The main function is that different models use different registers and are distinguished by a mask. This area can be read at will.
安规国家 | Safety countries | 2004 | Country_Code | U16 |  |  |  |  | RW | 安规国家，用于存储 | Safety regulation country for storing | [7 empty] | 写入时，固定的首地址为0x2004，长度为2 | When writing, the first address is fixed at 0x2004 and the length is 2.
安规版本 | Safety version | 2005 | Safety_Version | U16 |  |  |  |  | RW | 通讯主机（上位机）的安规参数版本号。 | version number of the safety parameter of the communication host (upper computer).
恢复出厂设置 | Restore factory settings | 2006 | Factory_Reset | U16 |  |  | 1 | 255 | RW | 恢复出厂寄存器； 位值为1有效。 Bit0：清除电量 Bit1：清除事件记录 Bit2：所有功能配置参数恢复默认值 读取时，返回上次写入操作的状态： 0x0000：成功 0x0001-0x00FF：正在操作 0xFFFB：操作失败，控制器拒绝响应（可能控制器正忙或配置错误） 0xFFFC：操作失败，控制器无应答 0xFFFD：操作失败，当前功能被禁止 0xFFFE：操作失败，参数存取失败 0xFFFF：操作失败，输入参数有误 | Restore factory register; A bit value of 1 is valid. Bit0: Clears the power level Bit1: Clears the event log Bit2: All function configuration parameters return to their default values When reading, return the status of the last write operation to 0x0000: successful 0x0001-0x00FF: operation in progress 0xFFFB: operation failed, controller refused to respond (possibly controller is busy or misconfigured) 0xFFFC: operation failed, no response from the controller 0xFFFD: operation failed, current function is disabled 0xFFFE: operation failed, parameter access failed 0xFFFF: operation failed, wrong parameter entered | [7 empty] | 写入时，固定的首地址为0x2006，长度为1 | Write with a fixed first address of 0x2006 and a length of 1
安规国家名称 | Safety country name | 2007 -- 200B | Safety_Name1 -- 5 | ASCII |  |  |  |  | RW | 安规国家名称第1-10位。每个地址表示2位，以下面为例，依次类推。 寄存器0x2007高8位存放安规名称第1位； 寄存器0x2007低8位存放安规名称第2位。 | Safety country name bits 1-10. Each address represents 2 bits, take the following as an example and so on. register 0x2007 high 8 bits holds bit 1 of the safety regulation name; Register 0x2007 low 8 bits holds the safety regulation name bit 2. | [7 empty] | 此区域内的数据暂时没使用,无意义 | The data in this area is not used at the moment and is meaningless
|  | 200C | [7 empty] | 预留 | Reserved
对上通讯协议设置 | Pair up communication protocol settings | 200D | Commu_protocol_type | U16 |  |  |  |  | RW | 协议设置寄存器： 0x0000:modbus_RTU协议； 0x0001:modbus_Korea协议； 0x0002:sofar_sgp_normal标准版协议； 0x0003:sofar_sgp_advance高级版协议； 0x0004:sunspec协议； 0x0005:solarmax协议； | Protocol setting registers: 0x0000:modbus_RTU protocol; 0x0001:modbus_Korea protocol; 0x0002:sofar_sgp_normal standard version protocol; 0x0003:sofar_sgp_advance advanced protocol; 0x0004:sunspec protocol; 0x0005:solarmax protocol;
安规文件包设置 | Safety compliance package setup | 200E | Country_Code_flash | U16 |  |  |  |  | RW | 安规标准，用于设置FLASH中的安规文件包 | Safety standard for setting the safety package in FLASH | [7 empty] | 写入时，固定的首地址为0x200E，长度为2 | When writing, the first address is fixed at 0x200E and the length is 2.
|  | 200F | Safety_Version_flash | U16 |  |  |  |  | RW | FLASH中的安规文件包版本号。 | The version number of the safety-compliant file package in FLASH.
|  | 2010 -- 2033 | [7 empty] | 预留 | Reserved
本地和远程 固件升级控制 | Local and remote Firmware Upgrade Control | 2034 | Remote_Download_Control_ex | U16 |  |  |  |  | W | 远程下载控制寄存器扩展。（只支持单个目标操作） 高字节。写入0xA5有效。 低字节包含需要升级的芯片组合，每个位的解释如下： Bit0：DCDC-ARM； Bit1：DCDC-DSP； | Remote download control register extension. (only single target operations are supported) High byte. Writing to 0xA5 is valid. The low byte contains the combination of chips to be upgraded and each bit is explained as follows: Bit0: DCDC-ARM; Bit1: DCDC-DSP; | [7 empty] | 此区域内的数据暂时没使用,无意义 | The data in this area is not used at the moment and is meaningless.
|  | 2035 | Remote_Upgrade_Control_ex | U16 |  |  |  |  | W | 远程升级控制寄存器扩展。（只支持单个目标操作） 高字节。写入0xA5有效。 低字节包含需要升级的芯片组合，每个位的解释如下： Bit0：DCDC-ARM； Bit1：DCDC-DSP； | Remote upgrade control register extension. (only a single target operation is supported) High byte. Writing to 0xA5 is valid. The low byte contains the combination of chips to be upgraded and each bit is explained as follows: Bit0: DCDC-ARM; Bit1: DCDC-DSP;
|  | 2036 | Local_Upgrade_Control_ex | U16 |  |  |  |  | W | 本地升级控制扩展1。 高字节。写入0xA5有效。 低字节包含需要升级的芯片组合，每个位的解释如下： Bit0：DCDC-ARM； Bit1：DCDC-DSP； | Local upgrade control extension 1. High byte. Writing to 0xA5 is valid. The low byte contains the combination of chips to be upgraded and each bit is explained as follows: Bit0: DCDC-ARM; Bit1: DCDC-DSP;
|  | 2037 | Local_Upgrade_Control2 | U16 |  |  |  |  | W | 本地升级控制扩展2。 高字节。写入0xA5有效。 低字节包含需要升级的文件类型，目前定义如下： 0x00：APP； 0x01：CORE； 0x02：预留； 0x03：预留； 0x04：安规文件； | Local upgrade control extension 2. High byte. Writing to 0xA5 is valid. The low byte contains the type of file to be upgraded and is currently defined as follows: 0x00: APP; 0x01: CORE; 0x02: reserved; 0x03: reserved; 0x04: safety file; | [7 empty] | 写入时，固定的首地址为0x2037，长度为1 | Write with a fixed first address of 0x2037 and a length of 1
|  | 2038 | Local_Upgrade_Status2 | U16 |  |  |  |  | R | 当前升级进度 高字节表示当前升级的目标文件类型： 0x00：APP； 0x01：CORE； 0x02：安规文件； 低字节表示当前升级进度：进度范围0-100%； | Current upgrade progress The high byte indicates the type of target file currently being upgraded: 0x00: APP; 0x01: CORE; 0x02: safety-compliant file; The low byte indicates the current upgrade progress: progress range 0-100%;
|  | 2039 | Upgrade_Total | U16 |  |  |  |  | R | 升级目标总数。 当使用同一固件对一个或多个目标同时升级时，该寄存器的值表示升级目标的总数量。 | Total number of upgrade targets. When upgrading one or more targets simultaneously using the same firmware, the value of this register indicates the total number of upgrade targets.
|  | 203A | Upgrade_Result_Table1 | U16 |  |  |  |  | R | 升级结果bit表1。 bit值为0表示升级未完成或失败； bit值为1表示升级成功。 最低位表示编号为1的升级目标。最高位表示编号为16的升级目标。 | Upgrade result bit table 1. A bit value of 0 indicates an incomplete or failed upgrade; A bit value of 1 indicates a successful upgrade. The lowest bit indicates an upgrade target numbered 1. The highest bit indicates an upgrade target numbered 16.
|  | 203B | Upgrade_Result_Table2 | U16 |  |  |  |  | R | 升级结果bit表2。 bit值为0表示升级未完成或失败； bit值为1表示升级成功。 最低位表示编号为17的升级目标。最高位表示编号为32的升级目标。 | Upgrade result bit table 2. A bit value of 0 indicates an incomplete or failed upgrade; A bit value of 1 indicates a successful upgrade. The lowest bit indicates an upgrade target numbered 17. The highest bit indicates the upgrade target numbered 32.
|  | 203C | Remote_Download_Control | U16 |  |  |  |  | W | 远程下载控制寄存器。（只支持单个目标操作） | Remote Download Control Register. (Only single target operations are supported) | [7 empty] | 高字节。写入0xA5有效。 低字节包含需要升级的芯片组合，每个位的解释如下： Bit0：通讯板； Bit1：控制板1（主DSP）； Bit2：控制板2（副DSP）； Bit3：Fuse； Bit4：BMS； Bit5：PCU； Bit6：BDU； Bit7：AFCI； | High byte. Writing to 0xA5 is valid. The low byte contains the combination of chips to be upgraded and each bit is explained as follows: Bit0: communication board; Bit1: control board 1 (main DSP); Bit2: control board 2 (sub-DSP); Bit3: Fuse; Bit4: BMS; Bit5: PCU; Bit6: BDU; Bit6: BDU; Bit7: AFCI;
|  | 203D | Remote_Upgrade_Control | U16 |  |  |  |  | W | 远程升级控制寄存器。 高字节： 单个BIN文件升级写入0xA5 sofar打包文件写入0x80 低字节： 低字节包含需要升级的芯片组合，参考《芯片角色和文件类型编码》文档，如果是sofar文件固定写入0xFF | Remote Upgrade Control Register. High Byte: Single BIN file upgrade writes 0xA5 sofar packaged files are written to 0x80 Low byte: The low byte contains the combination of chips to be upgraded, refer to the document Chip Roles and File Type Codes", if it is a sofar file fixed write 0xFF"
|  | 203E | Local_Upgrade_Control | U16 |  |  |  |  | W | 本地升级控制寄存器。（只支持单个目标操作），写入时，固定的首地址为0x203E，长度为1 | Local Upgrade Control Register. (only single target operations are supported), written with a fixed first address of 0x203E and a length of 1
|  | 203F | Local_Upgrade_Status | U16 |  |  |  |  | R | 当前升级进度 高字节表示当前升级的目标芯片： 0x00：不在升级状态； 0x01：主DSP升级； 0x02：副DSP升级； 0x03：ARM升级； 0x04：FUSE升级； 0x05：BMS升级； 0x06：PCU升级； 0x07：BDU升级； 0x28：DC/DC ARM升级； 0x29：DC/DC DSP升级； 0x42: AFCI升级 后续参考SVN《芯片角色和文件类型编码》 低字节表示当前升级进度：进度范围0-100%； | Current upgrade progress The high byte indicates the current upgrade target chip: 0x00: not in upgrade status; 0x01: primary DSP upgrade; 0x02: sub-DSP upgrade; 0x03: ARM upgrade; 0x04: FUSE upgrade; 0x05: BMS upgrade; 0x06: PCU upgrade; 0x07: BDU upgrade; 0x28: DC/DC ARM upgrade; 0x29: DC/DC DSP upgrade; 0x42: AFCI upgrade Refer to SVN Chip Role and File Type Coding" for follow-up | [7 empty] | 当此寄存器有值时，寄存器0x203D或者0x203E一定有一个有值 | When this register has a value, one of registers 0x203D or 0x203E must have a value
|  | 2040-2045 | Upgrade_Time | U16 |  |  |  |  | RW | 定时升级时间 寄存器0x2040:定时升级时间-年 寄存器0x2041:定时升级时间-月 寄存器0x2042:定时升级时间-日 寄存器0x2043:定时升级时间-时 寄存器0x2044:定时升级时间-分 寄存器0x2045:定时升级时间-秒 时间寄存器的值全是0XFF表示取消定时升级 | The low byte indicates the current upgrade progress: progress range 0-100%;"
|  | 2046 | Upgrade_Result | U16 |  |  |  |  | R | 升级结果 Bit0-Bit7： 本次升级的设备个数 Bit8-Bit15：本次升级结果是否统计完成 0xA5：结果统计完成 其它值：结果统计中 此字段值为0xA5时读取寄存器0x2047的升级结果才有效 此寄存器会在收到升级指令后重置 | Timed upgrade time Register 0x2040: Timed upgrade time - year Register 0x2041:Timed upgrade time - month Register 0x2042:Timed upgrade time - day Register 0x2043:Timed upgrade time - hour Register 0x2044:Timed upgrade time-minute Register 0x2045:Timed upgrade time-seconds The value of the time register is all 0XFF to cancel the timed upgrade
|  | 2047 | Upgrade_Result1 | U16 |  |  |  |  | R | 升级结果 设备升级成功个数 此寄存器会在收到升级指令后重置 | Upgrade result Bit0-Bit7: the number of devices upgraded this time Bit8-Bit15: whether the result of this upgrade is counted Bit8-Bit15: whether the result of this upgrade is completed Other values: results are being counted The value of this field is 0xA5 when the upgrade result of register 0x2047 is read. This register will reset after receiving the upgrade command
|  | 2048 | Upgrade_Result_target | U16 |  |  |  |  | W | 升级结果查询控制寄存器 APP和监控平台向该寄存器写入要查询的升级对象对应的编码，编码根据《芯片角色和文件类型编码》文档定义的编码为准 写入该寄存器后再从0x2046和0x2047寄存器获取升级结果 | Upgrade result Number of successful device upgrades This register will be reset after receiving an upgrade command
4.5PLC parameter area for power carrier communication(0x2100-0x3100)
|  | 2100 -- 2103 | AddressMask_Plc_Info | U64 |  |  |  |  | R | 本地址开始的64个寄存器地址字的掩码区。 参看地址0x0040的说明 | Mask area for the 64 register address words starting at this address. Refer to description of address 0x0040 | Installers | 00000000 | 0000000F |  |  |  |  | 用于区分哪些地址有效，哪些地址无效，主要作用就是不同机型使用的寄存器不同，通过掩码做区分。此块区域支持任意读取。 | It is used to distinguish which addresses are valid and which are not. The main function is that different models use different registers and are distinguished by a mask. This area can be read at will.
PLC主要参数设置 | Main PLC parameter settings | 2104 | PLC_Type | U16 | 1 |  |  |  | R | CCO和STA共用属性，PLC类型：隐藏属性，只需要显示数字 | Attribute shared by CCO and STA, PLC type: hidden attribute, only the number needs to be displayed
|  | 2105 -- 2113 | PLC_Soft_Ver1 -- 15 | ASCII | 1 |  |  |  | R | CCO和STA共用属性 PLC软件版本最大共30字节，ver1-15 | Attribute shared by CCO and STA PLC software version maximum total 30 bytes, ver1-15
|  | 2114 | PLC_Sta_Net_State | U16 | 1 |  |  |  | R | STA独有属性 PLC，STA读取网络状态，1-表示已入网，2-表示未入网；CCO读取时返回0 | Attributes unique to STA PLC, STA reads network status, 1- means networked, 2- means not networked; CCO returns 0 when read
|  | 2115 | PLC_Cco_Mac | U16 | 1 |  |  |  | R | STA独有属性 STA入网后的CCO地址，没有入网时，填全0，CCO设备访问，填全0 PLC的MAC地址共6字节，高2字节 寄存器高8位存放第1字节； 寄存器低8位存放第2字节。 | STA unique attribute CCO address after STA is on the network, fill in all 0s if not on the network, fill in all 0s for CCO device access The MAC address of the PLC is 6 bytes in total, 2 bytes high register high 8 bits holds byte 1; The low 8 bits of the register hold byte 2.
|  | 2116 |  | U16 | 1 |  |  |  | R | PLC的MAC地址共6字节，中2字节 寄存器高8位存放第3字节； 寄存器低8位存放第4字节。 | The MAC address of the PLC is 6 bytes in total, the middle 2 bytes register high 8 bits holds byte 3; Register low 8 bits holds byte 4.
|  | 2117 |  | U16 | 1 |  |  |  | R | PLC的MAC地址共6字节，低2字节 寄存器高8位存放第5字节； 寄存器低8位存放第6字节。 | The MAC address of the PLC totals 6 bytes, low 2 bytes register high 8 bits holds byte 5; Register low 8 bits holds byte 6.
|  | 2118 | PLC_Com_Property | U16 | 1 |  |  |  | RW | CCO和STA共用属性 bit0-bit1:0~1对应 1/1.5 bit2~bit4:0~7对应NONE/odd/EVEN三种校验方式 bit5~bit7 0~1 对应8/9两种数据位长度bit8~15 0~4 对应4800/9600/19200/38400/115200 | Attributes shared by CCO and STA bit0-bit1:0~1 corresponds to 1/1.5 bit2~bit4:0~7 corresponds to NONE/odd/EVEN three kinds of checksum bit5~bit7 0~1 corresponds to 8/9 two data bit lengths bit8~15 0~4 corresponds to 4800/9600/19200/38400/115200
|  | 2119 | PLC_Mac_Addr | U16 | 1 |  |  |  | RW | CCO和STA共用属性 PLC的MAC地址共6字节，高2字节 寄存器高8位存放第1字节； 寄存器低8位存放第2字节。 | CCO and STA shared attributes MAC address of PLC is 6 bytes in total, high 2 bytes The high 8 bits of the register hold the 1st byte; The low 8 bits of the register hold byte 2.
|  | 211A |  | U16 | 1 |  |  |  | RW | PLC的MAC地址共6字节，中2字节 寄存器高8位存放第3字节； 寄存器低8位存放第4字节。 | The MAC address of the PLC has a total of 6 bytes, 2 bytes in the middle register high 8 bits holds byte 3; Register low 8 bits holds byte 4.
|  | 211B |  | U16 | 1 |  |  |  | RW | PLC的MAC地址共6字节，低2字节 寄存器高8位存放第5字节； 寄存器低8位存放第6字节。 | The MAC address of the PLC totals 6 bytes, low 2 bytes register high 8 bits holds byte 5; Register low 8 bits holds byte 6.
|  | 211C | PLC_BandChnl | U16 | 1 |  |  |  | R(W) | CCO和STA共用属性，STA只读，CCO可读写 频段信息5个值，枚举：1/4/5/7/8 | CCO and STA share attributes, STA is read-only, CCO can read and write Band information 5 values, enumerated: 1/4/5/7/8
|  | 211D | PLC_TxPower | U16 | 1 |  |  |  | RW | CCO和STA共用属性 发射功率 高8位表示模拟功率，范围：0-10 低8位表示数字功率，范围：0-55(实际使用时减去40) | Attributes shared between CCO and STA Transmit power High 8 bits indicate analogue power, range: 0-10 Low 8 bits indicate digital power, range: 0-55 (minus 40 for actual use)
|  | 211E | PLC_Whitelist_ExeType | U16 | 1 |  |  |  | RW | CCO独有属性 白名单操作类型,只写寄存器，读取时返回0 1-删除全部白名单；2-删除列表白名单；3-写入列表白名单；4-读取白名单（用于定义下次读取白名单的起始编号和数量） | CCO unique attribute Whitelist operation type, write register only, returns 0 when read 1 - delete all whitelist; 2 - delete list whitelist; 3 - write list whitelist; 4 - read whitelist (used to define the starting number and number of the next whitelist read)
|  | 211F | PLC_WhitelistCount | U16 | 1 |  |  |  | RW | CCO独有属性 白名单总数量，最大30个 | CCO unique attributes Total number of whitelists, max 30
|  | 2120 | PLC_Whitelist_StartAndCount | U16 | 1 |  |  |  | RW | CCO独有属性 白名单操作开始编号和数量 高8位表示开始编号，范围1-30 低8位表示操作数量，范围1-5 | CCO unique attributes Start number and number of whitelist operations The high 8 bits indicate the start number, in the range 1-30 The lower 8 bits indicate the number of operations, in the range 1-5
PLC白名单 | PLC Whitelist | 2121 | PLC_Whitelist0 | U16 | 1 |  |  |  | RW | CCO独有属性 白名单0，高2字节 | CCO unique attribute Whitelist 0, high 2 bytes
|  | 2122 |  | U16 | 1 |  |  |  | RW | 白名单0，中2字节 | Whitelist 0, middle 2 bytes
|  | 2123 |  | U16 | 1 |  |  |  | RW | 白名单0，低2字节 | Whitelist 0, low 2 bytes
|  | 2124 | PLC_Whitelist1 | U16 | 1 |  |  |  | RW | 白名单1，高2字节 | Whitelist 1, high 2 bytes
|  | 2125 |  | U16 | 1 |  |  |  | RW | 白名单1，中2字节 | Whitelist 1, middle 2 bytes
|  | 2126 |  | U16 | 1 |  |  |  | RW | 白名单1，低2字节 | Whitelist 1, low 2 bytes
|  | 2127 | PLC_Whitelist2 | U16 | 1 |  |  |  | RW | 白名单2，高2字节 | Whitelist 2, high 2 bytes
|  | 2128 |  | U16 | 1 |  |  |  | RW | 白名单2，中2字节 | Whitelist 2, middle 2 bytes
|  | 2129 |  | U16 | 1 |  |  |  | RW | 白名单2，低2字节 | Whitelist 2, low 2 bytes
|  | 212A | PLC_Whitelist3 | U16 | 1 |  |  |  | RW | 白名单3，高2字节 | Whitelist 3, high 2 bytes
|  | 212B |  | U16 | 1 |  |  |  | RW | 白名单3，中2字节 | Whitelist 3, middle 2 bytes
|  | 212C |  | U16 | 1 |  |  |  | RW | 白名单3，低2字节 | Whitelist 3, low 2 bytes
|  | 212D | PLC_Whitelist4 | U16 | 1 |  |  |  | RW | 白名单4，高2字节 | Whitelist 4, high 2 bytes
|  | 212E |  | U16 | 1 |  |  |  | RW | 白名单4，中2字节 | Whitelist 4, middle 2 bytes
|  | 212F |  | U16 | 1 |  |  |  | RW | 白名单4，低2字节 | Whitelist 4, low 2 bytes
PLC复位 | PLC Reset | 2130 | PLC_Reset | U16 | 1 |  |  |  | W | CCO独有属性,只可写，1-表示模块复位 读取无意义返回数据0 | CCO unique attribute, write only, 1 - indicates module reset Read meaningless return data 0
五、Compatible with shared data areas(0x4E20-0x4FFF)
协议生效版本 | Versions of the agreement in force | 4E20 | VersionType | U16 |  |  | 0 | 1 | RW | 协议生效版本： 0：3代MODBUS; 1：4代MODBUS； | Protocol version in force: 0: 3 generation MODBUS. 1: Generation 4 MODBUS;
六、DCDC data area(0x5000-0x5FFF)
|  | 5000 -- 5003 | addressmask_dcdc_sysinfo | U64 |  |  |  |  | R | 本地址开始的64个寄存器地址字的掩码区。 参看地址0x0040的说明 | Mask area for the 64 register address words starting at this address. Refer to the description of address 0x0040 |  | 00000000 | 0000000F
DCDC版本号信息 | DCDC Version Number Information | 5004 | dcdc_arm_to_inv_485_ver | U16 |  |  |  |  | R | ARM对逆变器485协议版本 | ARM to inverter 485 protocol version
|  | 5005 | dcdc_dsp_to_inv_can_ver | U16 |  |  |  |  | R | DSP对逆变器CAN协议版本 | DSP to inverter CAN protocol version
|  | 5006 | dcdc_arm_to_dsp_232_ver | U16 |  |  |  |  | R | ARM对DSP内部232协议版本 | ARM to DSP internal 232 protocol version
|  | 5007 | dcdc_dsp_to_arm_232_ver | U16 |  |  |  |  | R | DSP对ARM内部232协议版本 | DSP to ARM internal 232 protocol version
|  | 5008 | dcdc_arm_to_bms_can_ver | U16 |  |  |  |  | R | ARM对电池CAN协议版本 | ARM to battery CAN protocol version
|  | 5009 | dcdc_dsp_to_bms_can_ver | U16 |  |  |  |  | R | DSP对电池CAN协议版本 | DSP to battery CAN protocol version
|  | 500A | dcdc_module_485_ver | U16 |  |  |  |  | R | DCDC模块间485协议版本 | DCDC inter-module 485 protocol version
|  | 500B -- 500E | dcdc_arm_app_software_ver0 -- 3 | ASCII |  |  |  |  | R | ARM app软件版本0-3（4个，8位ASCII） | ARM app software versions 0-3 (4, 8-bit ASCII)
|  | 500F -- 5010 | dcdc_arm_hardware_ver0 -- 1 | ASCII |  |  |  |  | R | ARM 硬件版本0-1（2个，4位ASCII） | ARM hardware version 0-1 (2, 4-bit ASCII)
|  | 5011 -- 5014 | dcdc_arm_boot_software_ver0 -- 3 | ASCII |  |  |  |  | R | ARM bootloader软件版本0-3（4个，8位ASCII） | ARM bootloader software versions 0-3 (4, 8-bit ASCII)
|  | 5015 | dcdc_arm_core | ASCII |  |  |  |  | R | ARM芯片代码（2位ASCII） | ARM Chip Code (2, 2-bit ASCII)
|  | 5016 -- 5019 | dcdc_dsp_app_software_ver0 -- 3 | ASCII |  |  |  |  | R | DSP app软件版本0-3（4个，8位ASCII） | DSP app software versions 0-3 (4, 8-bit ASCII)
|  | 501A -- 501B | dcdc_dsp_hardware_ver0 -- 1 | ASCII |  |  |  |  | R | DSP 硬件版本0-1（2个，4位ASCII） | DSP hardware version 0-1 (2, 4-bit ASCII)
|  | 501C -- 501F | dcdc_dsp_boot_software_ver0 -- 3 | ASCII |  |  |  |  | R | DSP bootloader软件版本0-3（4个，8位ASCII） | DSP bootloader software versions 0-3 (4, 8-bit ASCII)
|  | 5020 | dcdc_dsp_core | ASCII |  |  |  |  | R | DSP芯片代码（2位ASCII） | DSP chip code (2, 2-bit ASCII)
|  | 5021 -- 5024 | dcdc_safety_software_ver0 -- 3 | ASCII |  |  |  |  | R | 安规认证软件版本0-3（4个，8位ASCII） | Safety-certified software versions 0-3 (4, 8-bit ASCII)
|  | 5025 -- 5026 | dcdc_safety_hardware_ver0 -- 1 | ASCII |  |  |  |  | R | 安规认证硬件版本0-1（2个，4位ASCII） | Safety-certified hardware versions 0-1 (2, 4-bit ASCII)
|  | 5027 -- 5028 | dcdc_safety_library_ver0 -- 1 | U16 |  |  |  |  | R | 安规库版本0-1 | Safety-approved library version 0-1
DCDC设备SN号 | DCDC device SN number | 5029 -- 5032 | dcdc_serial_number0 -- 9 | ASCII |  |  |  |  | R | 设备SN号0-9（10个，20位） | Device SN number 0-9 (10, 20 digits)
|  | 5033 -- 5038 | dcdc_serial_number_ravd10 --15 | ASCII |  |  |  |  | R | 设备SN号预留10-15（6个，12位） | Device SN number reserved 10-15 (6, 12 digits)
DCDC基本信息和设置参数1 | DCDC basic information and setting parameters1 | 5039 | dcdc_pcu_mount_count | U16 |  |  |  |  | R | 本模块挂载PCU总数 | Total number of PCUs mounted in this module
|  | 503A | dcdc_bms_mount_count | U16 |  |  |  |  | R | 本模块挂载BMS总数 | Total number of BMS mounted on this module
|  | 503B | dcdc_parallel_count | U16 |  |  |  |  | R | 并联DCDC模块总数 | Total number of parallel DCDC modules
|  | 503C -- 503F | [7 empty] | 预留 | Reserved
|  | 5040 -- 5043 | addressmask_dcdc_rtinfo | U64 |  |  |  |  | R | 本地址开始的64个寄存器地址字的掩码区。 参看地址0x0040的说明 | Mask area for the 64 register address words starting at this address. Refer to the description of address 0x0040 |  | 00000000 | 0000000F
|  | 5044 | systime_year | U16 |  |  |  |  | RW | 系统时间-年 | System time - year
|  | 5045 | systime_month | U16 |  |  |  |  | RW | 系统时间-月 | System time - month
|  | 5046 | systime_date | U16 |  |  |  |  | RW | 系统时间-日 | System time - day
|  | 5047 | systime_hour | U16 |  |  |  |  | RW | 系统时间-时 | System time - hour
|  | 5048 | systime_minute | U16 |  |  |  |  | RW | 系统时间-分 | System time-minute
|  | 5049 | systime_second | U16 |  |  |  |  | RW | 系统时间-秒 | System time-second
|  | 504A | system_state | U16 |  |  |  |  | R | DCDC系统运行状态 0-休眠；1-待机；2-运行 | DCDC system operating status 0 - sleep; 1 - standby; 2 - running
|  | 504B | remote_on_off | U16 |  |  |  |  | RW | 远程开关机 低位：0x55-开机；0xAA-关机 | Remote power on/off Low: 0x55-On; 0xAA-Off
|  | 504C | forced_on_off | U16 |  |  |  |  | RW | 强制开关机 低位：0x55-开机；0xAA-关机 | Force power on/off Low: 0x55-On; 0xAA-Off
|  | 504D | fan_power_limit_percent | U16 |  |  |  |  | RW | 风扇限载功率百分比 | Fan load limit power percentage
|  | 504E | power_level | U16 |  |  |  |  | RW | 机型功率等级 0x01-5KW；其他-预留 | Model power level 0x01-5KW; other - reserved
|  | 504F | mode | U16 |  |  |  |  | RW | 充放电模式 0x0-待机；0x01-放电；0x02-充电 其他无效 | Charge and discharge mode 0x0-Standby; 0x01-Discharge; 0x02-Charge Other not valid
|  | 5050 | rt_power_control | U16 |  |  |  |  | RW | 实时功率控制 0x55-使能；0xAA-禁止 | Real-time power control 0x55-enable; 0xAA-disable
|  | 5051 | active_power_export_limit | U16 |  |  |  |  | RW | 输出最大有功功率百分比 | Output maximum active power percentage
|  | 5052 | dsp_state | U16 |  |  |  |  | R | DSP工作状态 0-Wait 等待 1-Check 检测 2-Normal 正常运行 3-RecoverFault 可恢复故障 4-PermenentFault 永久性故障 | DSP operating state 0-Wait Waiting 1-Check Detect 2-Normal Normal operation 3-RecoverFault Recoverable fault 4-PermenentFault Permanent fault
|  | 5053 | count_down | U16 | 1 | second |  |  | R | 开机倒计时 | Start-up countdown
|  | 5054 | low_bus_voltage | U16 | 0.1 | V |  |  | R | 低压侧母线电压 | Low-voltage side bus voltage
|  | 5055 | low_current | I16 | 0.1 | A |  |  | R | 低压侧电流 | Low voltage side current
|  | 5056 | low_power | I16 | 0.01 | kw |  |  | R | 低压侧功率 | Low side power
|  | 5057 | low_current_total | I16 | 0.1 | A |  |  | R | 低压侧总电流 | Total low voltage side current
|  | 5058 -- 505D | branch1_current -- dcdc_branch6_current -- | I16 | 0.1 | A |  |  | R | 支路1-6电流 | Tributary 1-6 current
|  | 505E -- 5063 | branch1_fly_cap_voltage -- dcdc_branch6_fly_cap_voltage | U16 | 0.1 | V |  |  | R | 支路1-6飞跨电容电压 | Tributary 1-6 flying across capacitor voltage
|  | 5064 | high_bus_voltage | U16 | 0.1 | V |  |  | R | 高压母线电压 | High voltage busbar voltage
|  | 5065 | insulation_impedance | U16 | 1 | kΩ |  |  | R | 绝缘阻抗 | Insulation impedance
|  | 5066 | inner_temperature | I16 | 1 | ℃ |  |  | R | 机箱内部环境温度 | Chassis internal ambient temperature
|  | 5067 | raditor_temperature | I16 | 1 | ℃ |  |  | R | 散热器温度 | Heat sink temperature
|  | 5068 | safety_recv_success_flag | U16 |  |  |  |  | R | 安规参数接收成功标志 0-失败;1-成功 | Safety parameter reception success flag 0-failure; 1 - success
|  | 5069 | power_limit_status | U16 |  |  |  |  | R | 功率限载状态 0-未限功； 1-指令限功； 2-Soc限功； 3-过温限功； | Power limit status 0-unlimited power; 1-Commanded power limited; 2-Soc power limiting; 3-Overtemperature power limiting;
|  | 506A -- 5073 | fault1 -- 10 | U16 |  |  |  |  | R | 故障字1-10（10个） | Fault words 1-10 (of 10)
|  | 5074 -- 507D | state1 -- 10 | U16 |  |  |  |  | R | 状态字1-10（10个） | Status words 1-10 (10)
|  | 507E -- 507F | [7 empty] | 预留 | Reserved
|  | 5080 -- 5083 | addressmask_dcdc_paras | U64 |  |  |  |  | R | 本地址开始的64个寄存器地址字的掩码区。 参看地址0x0040的说明 | Mask area for the 64 register address words starting at this address. Refer to the description of address 0x0040 |  | 00000000 | 0000000F
DCDC通讯参数 | DCDC communication parameters | 5084 | external_485_addr | U16 |  |  | 1 | 247 | RW | RS485外网地址（默认0x60） | RS485 external network address (default 0x60)
|  | 5085 | external_485_baudrate | U16 |  |  |  |  | RW | RS485外网波特率 0：1200bps 1：2400bps 2：4800bps 3：9600bps（默认） 4：19200bps 5：38400bps 6：57600bps 7：115200bps | RS485 external network baud rate 0: 1200bps 1: 2400bps 2: 4800bps 3: 9600bps (default) 4: 19200bps 5: 38400bps 6: 57600bps 7: 115200bps
|  | 5086 | external_485_stop_bit | U16 |  |  |  |  | RW | RS485外网停止位 0：1位停止位（默认） 1：1.5位停止位 2：2位停止位 | RS485 external network stop bits 0: 1 bit stop bit (default) 1: 1.5 bit stop bit 2: 2-bit stop bit
|  | 5087 | external_485_parity_bit | U16 |  |  |  |  | RW | RS485外网校验位 0：无校验/None（默认） 1：偶校验/Even 2：奇校验/Odd 3：高/Mark 4：低/Space | RS485 external network parity bit 0: No parity/None (default) 1: Even parity/Even 2: Odd parity/Odd 3: High/Mark 4: Low/Space
|  | 5088 | inner_485_addr | U16 |  |  | 1 | 247 | RW | RS485内网地址 | RS485 internal network address
|  | 5089 | inner_485_baudrate | U16 |  |  |  |  | RW | RS485内网波特率 | RS485 Intranet Baud Rate
|  | 508A | inner_485_stopbit | U16 |  |  |  |  | RW | RS485内网停止位 | RS485 Intranet Stop Bits
|  | 508B | inner_485_paritybit | U16 |  |  |  |  | RW | RS485内网校验位 | RS485 Intranet Check Bits
|  | 508C | arm_can_addr | U16 |  |  | 0x60 | 0x7F | RW | ARM CAN地址（默认0x60） | ARM CAN address (default 0x60)
|  | 508D | dsp_can_addr | U16 |  |  | 0x90 | 0x9F | RW | DSP CAN地址（默认0x90） | DSP CAN address (default 0x90)
|  | 508E | can_buad_rate | U16 |  |  |  |  | RW | CAN波特率 0：10Kbps 1：20Kbps 2：50Kbps 3：100Kbps 4：125Kbps 5：250Kbps 6：500Kbps（默认） 7：800Kbps 8：1Mbps | CAN Baud Rate 0: 10Kbps 1: 20Kbps 2: 50Kbps 3: 100Kbps 4: 125Kbps 5: 250Kbps 6: 500Kbps (default) 7：800Kbps 8: 1Mbps
DCDC基本信息和设置参数2 | DCDC basic information and setup parameters2 | 508F | mount_count | U16 |  |  |  |  | RW | DCDC挂载个数 | Number of DCDC mounts
|  | 5090 | mount_pcu_count | U16 |  |  |  |  | RW | PCU挂载个数 | Number of PCU mounts
|  | 5091 | mount_bms_count | U16 |  |  |  |  | RW | BMS挂载个数 | Number of BMS mounts
|  | 5092 | coding_state | U16 |  |  | 0 | 2 | R | 编码状态 0-未编码；1-正在编码；2-编码完成 | Encoding Status 0-not encoded; 1-encoding in progress; 2-encoding complete
|  | 5093 -- 509F | [7 empty] | 预留 | Reserved
DCDC基本信息和设置参数3 | DCDC basic information and setup parameters 3 | 50A0 | connect_waittime | U16 | 1 | second |  |  | RW | 并网等待时间 | Grid connection waiting time
|  | 50A1 | rated_voltage | U16 | 0.1 | V |  |  | RW | 电网额定电压 | Grid rated voltage
|  | 50A2 | rated_freq | U16 | 0.01 | Hz |  |  | RW | 电网额定频率 | Grid rated frequency
|  | 50A3 | phase_number | U16 |  |  |  |  | RW | 电网相数 1-单相;3-三相 | Number of grid phases 1-single-phase;3-three-phase
|  | 50A4 | gfci_limit | U16 | 1 | mA |  |  | RW | DCDC漏电流保护值，用于计算绝缘阻抗 | DCDC leakage current protection value for calculation of insulation impedance
|  | 50A5 | power_up_time | U16 | 1 | ms |  |  | RW | 0功率上升到额定功率时间 | 0 power rise time to rated power
|  | 50A6 | power_down_time | U16 | 1 | ms |  |  | RW | 额定功率上升到0功率时间 | Rated power rise to 0 power time
七、PCU & BDU data area(0x6000-0x6FFF)
|  | 6000 -- 6003 | AddressMask_PCU1 | U64 |  |  |  |  | R | 本地址开始的64个寄存器地址字的掩码区。 参看地址0x0040的说明 | Mask area for the 64 register address words starting at this address. Refer to the description of address 0x0040 |  | 00000000 | 0000000F
|  | 6004 | PCU_Number | [5 empty] | R | PCU在线总数。 | Total number of PCUs online.
|  | 6005 -- 600F | [6 empty] | R | 汇总信息预留（11个） | Aggregate information reserved (11)
|  | 6010 | PCU_ID | U16 |  |  |  |  | R | PCU编号。 | PCU number. | [7 empty] | 多机系统中各PCU的编号，编号从1开始。 | Numbering of each PCU in a multi-machine system, numbering starts from 1.
|  | 6011 -- 601A | PCU_SN0 -- 9 | ASCII |  |  |  |  | R | PCU序列号0-9（10个） | PCU serial number 0-9 (10) | [7 empty] | PCU成品序列号，ASCII码形式，案例请查看0x6011地址说明。 例:0x5043代表"PC" | PCU serial number, ASCII form, see 0x6011 address description for example. Example: 0x5043 for "PC"
|  | 601B -- 601C | PCU_Software_Version1 -- 2 | ASCII |  |  |  |  | R | 软件版本号1-2 | Software version number 1-2 | [7 empty] | PCU版本信息，例:软件版本V010012，硬件版本:0200,CAN协议版本:0102 | PCU version information, e.g. software version V010012, hardware version:0200,CAN protocol version:0102
|  | 601D | PCU_Hardware_Version | U16 |  |  |  |  | R | 硬件版本号 | Hardware version number
|  | 601E | PCU_Can1_Version | U16 |  |  |  |  | R | CAN1协议版本号 | CAN1 protocol version number
|  | 601F | PCU_Can2_Version | U16 |  |  |  |  | R | CAN2协议版本号 | CAN2 protocol version number
|  | 6020 | PCU_Work_State | U16 |  |  |  |  | R | 模块状态 0：Update 1：Check 2：Normal 3：Active 4：Fault 5：Permanent Fault | Module Status 0: Update 1: Check 2: Normal 3: Active 4: Fault 5: Permanent Fault | [7 empty] | Update:软件升级状态 Check:自检状态，PCU初始状态 Normal:正常充放电运行状态 Active:激活BMS状态 Fault:可恢复故障状态，达到特定条件可恢复的故障 Permanent Fault:永久性故障状态，不可恢复 | Update:Software update status Check:self-test status, PCU initial status Normal:Normal charging and discharging state Active:BMS active Fault:Recoverable fault state, a fault that can be recovered under certain conditions Permanent Fault:Permanent fault state, not recoverable
|  | 6021 | PCU_Internal_Temperature | U16 | 1 | ℃ |  |  | R | 机箱内部温度 | Chassis internal temperature | [7 empty] | 例：0x0001指机箱内温度1为1℃ | Example: 0x0001 means that the temperature inside the case1 is 1°C
|  | 6022 | PCU_Radiator_Temperature1 | I16 | 1 | ℃ |  |  | R | 散热器1温度 | Heatsink 1 temperature | [7 empty] | 例：0x0001指散热器温度1为1℃ | Example: 0x0001 means that the heat sink temperature1 is 1°C
|  | 6023 | PCU_Radiator_Temperature2 | I16 | 1 | ℃ |  |  | R | 散热器2温度(预留，未使用) | Heatsink 2 temperature (reserved, not used)
|  | 6024 -- 6027 | PCU_Warning1 -- 4 | U16 |  |  |  |  | R | 警告1-4 例：0x4000指禁止放电警告 | Warning 1-4 Example: 0x4000 means forbidden discharge warning | [7 empty] | 记录PCU的故障信息，对应故障信息见“PCU故障位说明”，案例请查看0x6024地址说明 | Record the fault information of the PCU, see "PCU Fault Bit Description" for the corresponding fault information, see 0x6024 address description for the case
|  | 6028 -- 602B | PCU_Fault1 -- 4 | U16 |  |  |  |  | R | 故障1-4 例：0x0001指散热器过温保护 | Fault 1-4 Example: 0x0001 refers to radiator overtemperature protection
|  | 602C | PCU_DC_High_Voltage | U16 | 0.1 | V | 0 |  | R | DC高压侧电压 | DC high voltage side voltage | [7 empty] | PCU高压侧电压，例:0x0FD3代表405.1V | PCU high voltage side voltage, for example:0x0FD3 represents 405.1V
|  | 602D | PCU_DC_Low_Voltage | U16 | 0.1 | V | 0 |  | R | DC低压侧电压 | DC low-voltage side voltage | [7 empty] | 低压电池电压，例:0x0214代表53.2V | Low voltage battery voltage, e.g. 0x0214 for 53.2V
|  | 602E | PCU_Low_Current | I16 | 0.1 | A |  |  | R | DC低压侧电流 | DC low voltage side current | [7 empty] | 低压电池电流，充电为正，放电为负 例:0xFFAF代表放电5.1A | Low voltage battery current, charging is positive, discharging is negative Example:0xFFAF for 5.1A discharge
|  | 602F | PCU_Low_Power | I16 | 0.01 | kW |  |  | R | DC低压侧功率 | DC low-voltage side power | [7 empty] | 低压电池输出功率，充电为正，放电为负 例:0x0F8C5代表放电1851W | Low voltage battery output power, charging is positive, discharging is negative Example:0x0F8C5 represents 1851W discharged
|  | 6030 | PCU_BusP | U16 | 0.1 | V |  |  | R | 正母线电压 | Positive bus voltage | [7 empty] | 未使用 | Not used
|  | 6031 | PCU_BusN | U16 | 0.1 | V |  |  | R | 负母线电压 | Negative busbar voltage
|  | 6032 -- 6035 | PCU_FC_Voltage1 -- 4 | U16 | 0.1 | V |  |  | R | 飞跨电容电压1-4 | Fly across capacitor voltage 1-4
|  | 6036 -- 6039 | PCU_IL_Current1 -- 4 | I16 | 0.1 | A |  |  | R | 电感电流支路1-4 | Inductive current branch 1-4
|  | 603A -- 603F | [7 empty] | 预留 | Reserved
|  | 6040 -- 6043 | AddressMask_PCU2 | U64 |  |  |  |  | R | 本地址开始的64个寄存器地址字的掩码区。 参看地址0x0040的说明 | Mask area for the 64 register address words starting at this address. Refer to description of address 0x0040 |  | 00000000 | 0000000F
|  | 6044 | PCU_Inquire | U16 |  |  | 1 | 32 | RW | PCU查询控制字。 通过设置该寄存器来选择需要读取或设置的PCU模块。 | PCU query control word. Select the PCU module to be read or set by setting this register. | [7 empty] | 通过该控制字来查询特定编号的PCU模块 | The control word is used to query the PCU module for a specific number
|  | 6045 | PCU_Remote_On_Off | U16 |  |  | 0 | 3 | RW | 直流模块远程开关机 0：关机 1：禁止充电 2：禁止放电 3：允许充电、放电 | DC module remote switch on/off 0: Power off 1: charging disabled 2: Discharge prohibited 3: Charging and discharging allowed | [7 empty] | 未使用 | Not used
|  | 6046 | PCU_Max_Charge_Current | U16 | 0.1 | A | 0 | 65535 | RW | 直流模块最大充电电流 | Max. charging current of the DC module | [7 empty] | 未使用 | Not used
|  | 6047 | PCU_Max_Discharge_Current | U16 | 0.1 | A | 0 | 65535 | RW | 直流模块最大放电电流 | Max. discharge current of the DC module
|  | 6048 | K_Voltage_HVbus | U16 | 0.001 | p.u. | 950 | 1050 | RW | 高压侧hvbus电压校准比例 例:0x03D5代表0.981 | Calibration ratio for hvbus voltage on the high voltage side Example:0x03D5 stands for 0.981 | [7 empty] | 用来校准PCU采样值，案例请查看0x6048地址说明 | Used to calibrate PCU sample values, see 0x6048 address description for examples
|  | 6049 | K_Voltage_Pbus | U16 | 0.001 | p.u. | 950 | 1050 | RW | 高压侧pbus电压校准比例 | High-voltage side pbus voltage calibration ratio
|  | 604A | K_Current_HV_Chg | U16 | 0.001 | p.u. | 950 | 1050 | RW | 高压侧充电电流校准比例 | High voltage side charge current calibration ratio
|  | 604B | K_Current_HV_Dchg | U16 | 0.001 | p.u. | 950 | 1050 | RW | 高压侧放电电流校准比例 | High-voltage side discharge current calibration ratio
|  | 604C | K_Voltage_LV | U16 | 0.001 | p.u. | 950 | 1050 | RW | 低压侧电压校准比例 | Low voltage side voltage calibration ratio
|  | 604D | K_Current_LV_Chg | U16 | 0.001 | p.u. | 950 | 1050 | RW | 低压侧充电电流校准比例 | Low voltage side charge current calibration ratio
|  | 604E | K_Current_LV_Dchg | U16 | 0.001 | p.u. | 950 | 1050 | RW | 低压侧放电电流校准比例 | Low voltage side discharge current calibration ratio
|  | 604F -- 607F | [7 empty] | 预留 | Reserved
|  | 6080 -- 6083 | AddressMask_BDU1 | U64 |  |  |  |  | R | 本地址开始的64个寄存器地址字的掩码区。 参看地址0x0040的说明 | Mask area for the 64 register address words starting at this address. Refer to description of address 0x0040 |  | 00000000 | 0000000F
BDU信息 | BDU information | 6084 | BDU_Number | U16 |  |  |  |  | R | BDU在线总数。 | Total number of BDUs online.
|  | 6085 -- 608F | [6 empty] | R | 汇总信息预留（11个） | Aggregate information reserved (11)
|  | 6090 | BDU_ID | U16 |  |  |  |  | R | BDU编号。 编号从1开始。 | BDU numbering. Numbering starts from 1.
|  | 6091 -- 609A | BDU_SN0 -- 9 | ASCII |  |  |  |  | R | BDU序列号0-9（10个） | BDU serial number 0-9 (10)
|  | 609B | Software_Version_Stage_BDU | ASCII |  |  |  |  | R | BDU芯片软件版本号阶段定义位。 寄存器低8位存放ASCII码。正式版本的默认值为'V'。 | BDU chip software version number phase definition bits. The lower 8 bits of the register hold the ASCII code. The default value for the official version is 'V'.
|  | 609C | Software_Version_Major_BDU | ASCII |  |  |  |  | R | BDU芯片软件主版本号。 同一个系统中所有芯片主版本号必须一致，否则视为系统故障。 寄存器高8位存放高位数字； 寄存器低8位存放低位数字。 | BDU Chip Software Master Version Number. All chip master version numbers in the same system must be the same, otherwise it is considered a system fault. The high 8 bits of the register hold the high digits; The lower 8 bits of the register hold the lower digits.
|  | 609D | Software_Version_Custom_BDU | ASCII |  |  |  |  | R | BDU芯片软件非标定制版本号。 正标软件此版本号为"00"。同一个系统中所有芯片非标定制版本号必须一致，否则视为系统故障。 寄存器高8位存放高位数字； 寄存器低8位存放低位数字。 | BDU chip software non-standard custom version number. Genuine software this version number is "00". All chips in the same system non-standard custom version number must be the same, otherwise it is considered as system failure. The high 8 bits of the register hold the high digit; The lower 8 bits of the register hold the lower digits.
|  | 609E | Software_Version_Minor_BDU | ASCII |  |  |  |  | R | BDU芯片软件子版本号。 寄存器高8位存放高位数字； 寄存器低8位存放低位数字。 | BDU chip software sub-version number. Register high 8 bits to hold high digits; Register low 8 bits hold low digits.
|  | 609F | BDU_Fault1 | U16 |  |  |  |  | R | BDU故障信息1 | BDU fault message 1
|  | 60A0 | BDU_Battery_Number | U16 |  |  |  |  | R | 单簇电池数量 | Number of cells in a single cluster
|  | 60A1 | TotalNum_PV | U16 | 1 |  |  |  | R | 组串总路数 | Total number of strings
|  | 60A2 | TotalNum_Battery | U16 | 1 |  |  |  | R | 电池总路数 | Total number of battery circuits
|  | 60A3 -- 60A5 | [7 empty] | 预留 | Reserved
|  | 60A6 -- 60A9 | AddressMask_BDU2 | U64 |  |  |  |  | R | 本地址开始的64个寄存器地址字的掩码区。 参看地址0x0040的说明 | Mask area for the 64 register address words starting at this address. Refer to the description of address 0x0040 |  | 00000000 | 0000000F
|  | 60AA | BDU_Inquire | U16 |  |  | 1 |  | RW | BDU查询控制字。 通过设置该寄存器来选择需要读取或设置的BDU模块。 | BDU lookup control word. Select the BDU module to be read or set by setting this register.
|  | 60AB | RatedPower_N_ID | U16 | 1 |  | 255 |  | RW | 操作指定路数的编号，取值在组串总路数以内, 从1开始 | Operate the number of the specified number of circuits, taking values up to the total number of circuits in the string, starting from 1
|  | 60AC | RatedPower_N_PV | U16 | 1 |  |  |  | R | 指定路数的组串额定功率 | The string power rating for the specified number of circuits
|  | 60AD | RatedPower_N_Battery | U16 | 1 |  |  |  | R | 指定路数的电池额定功率 | Battery power rating for the specified number of circuits
八、ODM data customisation area(0x7000-0x707F)
自定义 序列号、机型 | Custom Serial number, model | 7000 |  | ASCII |  |  |  |  | RW | 0x7000-0x707F的地址为自定义区域，需满足以下格式： 本区所有寄存器均为ASCII格式，寄存器高8位存储前端字符，低8位存储后端字符。如字符串“1234”存储在0x7000、0x7001中时，0x7000中的数据为0x3132；0x7001中的数据为0x3334。 允许的字符包括：0x20-0x7E和0xFF。0xFF在解析时自动忽略。 字符串格式定义如下： 键1=值1\r\n键2=值2\r\n 该协议版本支持的键有：“SN”：ODM序列号“machine”：ODM机型 | "The addresses 0x7000-0x707F are custom areas subject to the following format: All registers in this area are in ASCII format, with the high 8 bits of the register storing the front-end characters and the low 8 bits storing the back-end characters. If the string "1234" is stored in 0x7000 and 0x7001, the data in 0x7000 will be 0x3132; the data in 0x7001 will be 0x3334. Allowed characters are 0x20-0x7E and 0xFF. 0xFF is automatically ignored during parsing. The string format is defined as follows: Key 1 = value 1 \r\n Key 2 = value 2 \r\n The keys supported by this protocol version are: "SN": ODM serial number "machine": ODM model" | End-users | [6 empty] | ODM区： 注1：写入要U16对齐，不够补0x00; 注2：清除需要用0xFF写入覆盖; 注3：工厂模式下才能进行写操作; 注4：可以只写SN,或只写machine; 注5：不支持单寄存器读写，只支持整块读写； | ODM area: Note 1: Write to be U16 aligned, not enough to make up 0x00. Note 2: Clear needs to be overwritten with 0xFF writes. Note 3: Write operations can only be performed in factory mode. Note 4: You can write only SN, or write only machine. Note 5: Single register read/write is not supported, only whole block read/write is supported;
九、BMS transmissive area（0x9000-0x9FFF）
|  | 9000 -- 9003 | AddressMask_BMS1_System | U64 |  |  |  |  | R | 本地址开始的64个寄存器地址字的掩码区。 参看地址0x0040的说明 | Mask area for the 64 register address words starting at this address. Refer to the description of address 0x0040 |  | 00000000 | 0000000F
BMS基本信息 | Basic BMS information | 9004 | BMS_Sys_Time | U32 |  |  |  |  | R | BMS系统时钟 Bit0-5：second，范围0-59 Bit6-11：minute，范围0-59 Bit12-16：hour，范围0-23 Bit17-21：day，范围1-31 Bit22-25：month，范围1-12 Bit26-31：year，范围0-63（起始于2000年） | BMS system clock Bit0-5: second, range 0-59 Bit6-11: minute, range 0-59 Bit12-16: hour, range 0-23 Bit17-21: day, range 1-31 Bit22-25: month, range 1-12 Bit26-31: year, range 0-63 (from the year 2000)
9005
|  | 9006 | BMS_CAN_Version | U16 |  |  |  |  | R | CAN协议版本号 | CAN protocol version number
|  | 9007 | BMS_Manufacture_Name0 | U16 |  |  |  |  | R | 厂商信息0 例:0x414D代表"AM" | Manufacturer information 0 Example:0x414D stands for "AM"
|  | 9008 -- 900A | BMS_Manufacture_Name1 -- 3 | U16 |  |  |  |  | R | 厂商信息1-3 | Manufacturer information 1-3
|  | 900B | BMS_Version | U16 |  |  |  |  | R | BMS版本号 | BMS version number
|  | 900C | Cell_Type | U16 |  |  |  |  | R | 电芯类型 | Cell type
|  | 900D | BaPack_Number | U16 |  |  |  |  | R | 高8位：电池组并机数 低8位：所有电池包电池串数 | High 8 bits: number of battery pack cells in parallel Low 8 bits: number of strings of all battery packs
|  | 900E | Realtime_Capacity | U16 | 1 | % |  |  | R | 实时剩余容量 | Real-time remaining capacity
|  | 900F | Total_Voltage | U16 | 0.1 | V |  |  | R | 总电压 | Total voltage
|  | 9010 | Total_Current | I16 | 0.1 | A |  |  | R | 总电流 | Total current
|  | 9011 | Cell_Average_Temperature | U16 | 0.1 | ℃ |  |  | R | 电芯平均温度 | Average cell temperature
|  | 9012 | SOC | U16 | 1 | % |  |  | R | 荷电状态 | Charge status
|  | 9013 | SOH | U16 | 1 | % |  |  | R | 健康度 | Health
BMS保护、告警信息 | BMS protection, alarm information | 9014 -- 9015 | BMS_Sys_Protect0 -- 1 | U16 |  |  |  |  | R | BMS系统保护信息0-1 | BMS protection message 0-1
|  | 9016 -- 9017 | BMS_Sys_Alarm0 -- 1 | U16 |  |  |  |  | R | BMS系统告警信息0-1 | BMS system alarm message 0-1
BMS版本号 | BMS version number | 9018 | Sofar_BMS_Version | ASCII |  |  |  |  | R | 寄存器低8位存放ASCII码,正式版本的默认值为'V'。 | The low 8 bits of the register hold the ASCII code, the default value for the official version is 'V'.
|  | 9019 | Sofar_BMS_Version | U16 |  |  |  |  | R | 寄存器低8位为软件大版本号0-255 | Register low 8 bits for software major version number 0-255
|  | 901A | Sofar_BMS_Version | U16 |  |  |  |  | R | 寄存器低8位为软件非标版本号0-255 | Register low 8 bits for software non-standard version number 0-255
|  | 901B | Sofar_BMS_Version | U16 |  |  |  |  | R | 寄存器低8位为软件小版本号0-255 | The lower 8 bits of the register hold the software minor version number 0-255
|  | 901C -- 901F | [7 empty] | 预留 | Reserved
BMS查询控制字 | BMS query control word | 9020 | BMS_Inquire | U16 |  |  |  |  | RW | 电池查询控制字 Bit0-7：查询的电池Pack序号，有效范围0~15，0表示第1包电池 Bit8-11:查询的电池组序号，有效范围0~15，0表示第1组电池 Bit12-15：查询的故障序号，有效范围0~5，0表示最近的一次故障 | Battery Query Control Word Bit0-7:Queryed battery pack serial number, valid range 0~15, 0 means the 1st pack battery Bit8-11:Queryed battery pack serial number, valid range 0~15, 0 means the 1st pack Bit12-15:Query fault number, valid range 0~5, 0 means the latest fault
|  | 9021 -- 903F | [7 empty] | 预留 | Reserved
|  | 9040 -- 9043 | AddressMask_BMS2_Realtime | U64 |  |  |  |  | R | 本地址开始的64个寄存器地址字的掩码区。 参看地址0x0040的说明 | mask area for the 64 register address words starting at this address. Refer to the description of address 0x0040 |  | 00000000 | 0000000F
电池包 实时数据 | Battery pack Real-time data | 9044 | Pack_RT_ID | U16 |  |  |  |  | R | 实时数据电池包编号。 高8位：电池包组序号 低8位：电池包包序号 | Real time data battery pack number. High 8 bits: battery pack serial number Low 8 bits: battery pack pack serial number
|  | 9045 | Pack_RT_Timestamp | U32 |  |  |  |  | R | 实时数据时间戳 Bit0-5：second，范围0-59 Bit6-11：minute，范围0-59 Bit12-16：hour，范围0-23 Bit17-21：day，范围1-31 Bit22-25：month，范围1-12 Bit26-31：year，范围0-63（起始于2000年） | Real-time data timestamp Bit0-5: second, range 0-59 Bit6-11: minute, range 0-59 Bit12-16: hour, range 0-23 Bit17-21: day, range 1-31 Bit22-25: month, range 1-12 Bit26-31: year, range 0-63 (from the year 2000)
9046
|  | 9047 | Pack_RT_SN0 | U16 |  |  |  |  | R | 设备RT序列号0（ASCII） 例:0x5043代表"PC" | Device RT serial number 0 (ASCII) Example:0x5043 stands for "PC"
|  | 9048 -- 9050 | Pack_RT_SN1 -- 9 | U16 |  |  |  |  | R | 设备序列号1-9 | Device serial number 1-9
|  | 9051 -- 9068 | Pack_RT_Cell_Voltage1 -- 24 | U16 | 0.001 | V |  |  | R | 电芯RT 1-24电压 | Cell RT 1-24 Voltage
|  | 9069 | Pack_RT_Cell_Max_Voltage | U16 | 0.001 | V |  |  | R | 电芯最高电压 | Cell maximum voltage
|  | 906A | Pack_RT_Cell_Min_Voltage | U16 | 0.001 | V |  |  | R | 电芯最低电压 | Cell min voltage
|  | 906B -- 906E | Pack_RT_Temperature1_Pack -- Pack_RT_Temperature4_Pack | I16 | 0.1 | ℃ |  |  | R | 电池包RT温度1-4 | Battery pack RT temperature 1-4
|  | 906F | Pack_RT_Temperature_MOS | I16 | 0.1 | ℃ |  |  | R | MOS管温度 | MOS tube temperature
|  | 9070 | Pack_RT_Temperature_Env | I16 | 0.1 | ℃ |  |  | R | 电池包内环境温度 | Battery pack internal ambient temperature
|  | 9071 | Pack_RT_Current | I16 | 0.1 | A |  |  | R | 电池包电流 | Battery pack current
|  | 9072 | Pack_RT_Remaining_Capacity | U16 | 0.1 | Ah |  |  | R | 剩余容量 | Remaining capacity
|  | 9073 | Pack_RT_FullCharge_Capacity | U16 | 0.1 | Ah |  |  | R | 满充容量 | Full charge capacity
|  | 9074 | Pack_RT_Cycles | U16 | 1 | times |  |  | R | 循环次数 | Number of cycles
|  | 9075 | Pack_RT_Balance_State | U16 |  |  |  |  | R | 均衡状态 Bit0-15：对应第1-16节电芯的均衡状态 0：均衡关闭，1：均衡开启 | Equalisation status Bit0-15: equalisation status corresponding to cells 1-16 0: equalisation off, 1: equalisation on
|  | 9076 | Pack_RT_Alarm_State | U16 |  |  |  |  | R | 告警状态 | Alarm status
|  | 9077 | Pack_RT_Protect_State | U16 |  |  |  |  | R | 保护状态 | Protection status
|  | 9078 | Pack_RT_Fault_State | U16 |  |  |  |  | R | 故障状态 | Fault status
|  | 9079 | Pack_RT_Total_Voltage | U16 | 0.1 | V |  |  | R | 总电压 | Total voltage
|  | 907A | Pack_RT_SOC | U16 | 1 | % |  |  | R | SOC | SOC
|  | 907B | Pack_RT_Pack_Number | U16 |  |  |  |  | R | 本组电池的电池包总串数 | Total number of battery pack strings for this group of batteries
|  | 907C | Pack_RT_Cell_Number | U16 |  |  |  |  | R | 本组单个电池包的电池单体串数 | Number of individual strings of batteries in this group of individual packs
|  | 907D -- 907F | [7 empty] | 预留 | Reserved
|  | 9080 -- 9083 | AddressMask_BMS3_Fault | U64 |  |  |  |  | R | 本地址开始的64个寄存器地址字的掩码区。 参看地址0x0040的说明 | Mask area for the 64 register address words starting at this address. Refer to the description of address 0x0040 |  | 00000000 | 0000000F
电池包 故障数据 | Battery pack Fault data | 9084 | Pack_Fault_ID | U16 |  |  |  |  | R | 实时故障电池包编号。 Bit0-7：查询的电池Pack序号，有效范围0~15，0表示第1包电池 Bit8-11:查询的电池组序号，有效范围0~15，0表示第1组电池 Bit12-15：查询的故障序号，有效范围0~5，0表示最近的一次故障 | Real-time faulty battery pack number. Bit0-7:Queried battery Pack serial number, valid range 0~15, 0 means the 1st battery pack Bit8-11:Queried battery pack serial number, valid range 0~15, 0 means the 1st battery pack Bit12-15:Queried fault serial number, valid range 0~5, 0 means the latest fault
|  | 9085 -- 9086 | Pack_Fault_Timestamp | U32 |  |  |  |  | R | 故障数据时间戳 Bit0-5：second，范围0-59 Bit6-11：minute，范围0-59 Bit12-16：hour，范围0-23 Bit17-21：day，范围1-31 Bit22-25：month，范围1-12 Bit26-31：year，范围0-63（起始于2000年） | Fault data time stamp Bit0-5：second, range 0-59 Bit6-11: minute, range 0-59 Bit12-16: hour, range 0-23 Bit17-21: day, range 1-31 Bit22-25: month, range 1-12 Bit26-31: year, range 0-63 (from the year 2000)
|  | 9087 -- 9090 | Pack_Fault_SN0 -- 9 | U16 |  |  |  |  | R | 设备Fault序列号0-9 | Device Fault serial number 0-9
|  | 9091 -- 90A8 | Pack_Fault_Cell_Voltage1 -- 24 | U16 | 0.001 | V |  |  | R | 电芯Fault 1-24电压 | Cell Fault 1-24 voltage
|  | 90A9 | Pack_Fault_Cell_Max_Voltage | U16 | 0.001 | V |  |  | R | 电芯最高电压 | Cell maximum voltage
|  | 90AA | Pack_Fault_Cell_Min_Voltage | U16 | 0.001 | V |  |  | R | 电芯最低电压 | Cell Min Voltage
|  | 90AB -- 90AE | Pack_Fault_Temperature1_Pack -- Pack_Fault_Temperature4_Pack | I16 | 0.1 | ℃ |  |  | R | 电池包Fault温度1-4 | Battery pack Fault temperature 1-4
|  | 90AF | Pack_Fault_Temperature_MOS | I16 | 0.1 | ℃ |  |  | R | MOS管温度 | MOS tube temperature
|  | 90B0 | Pack_Fault_Temperature_Env | I16 | 0.1 | ℃ |  |  | R | 电池包内环境温度 | Ambient temperature inside battery pack
|  | 90B1 | Pack_Fault_Current | I16 | 0.1 | A |  |  | R | 电池包电流 | Battery pack current
|  | 90B2 | Pack_Fault_Remaining_Capacity | U16 | 0.1 | Ah |  |  | R | 剩余容量 | Remaining capacity
|  | 90B3 | Pack_Fault_FullCharge_Capacity | U16 | 0.1 | Ah |  |  | R | 满充容量 | Full Charge Capacity
|  | 90B4 | Pack_Fault_Total_Voltage | U16 | 0.01 | V |  |  | R | 总电压 | Total voltage
|  | 90B5 | Pack_Alarm_State | U16 |  |  |  |  | R | 告警状态 | Alarm status
|  | 90B6 | Pack_Protect_State | U16 |  |  |  |  | R | 保护状态 | Protection status
|  | 90B7 | Pack_Fault_State | U16 |  |  |  |  | R | 故障状态 | Fault status
|  | 90B8 | Pack_Fault_Pack_Number | U16 |  |  |  |  | R | 本组电池的电池包总数 | Total number of packs in this group of batteries
|  | 90B9 | Pack_Fault_Cell_Number | U16 |  |  |  |  | R | 本组单个电池包的电池单体串数 | Number of individual battery strings in this group of individual packs
Note on H444: PF1VK175: -10000~-8000对应功率因数-1~-0.8
Note on I444: PF1VK175: 8000~10000对应功率因数0.8~1

## Fault Bit Field Description
Table | Byte | Bit | Bit Fields | No. | 备注 | Remarks | Alarm sources | 分类 | 设计归类
Fault1 | byte 0 | bit 0 | GridOVP | 001 | 电网过压 | Grid over-voltage | DSP | 外部 | 电网
|  | bit 1 | GridUVP | 002 | 电网欠压 | Grid undervoltage | DSP | 外部
|  | bit 2 | GridOFP | 003 | 电网过频 | Grid overfrequency | DSP | 外部
|  | bit 3 | GridUFP | 004 | 电网欠频 | Grid underfrequency | DSP | 外部
|  | bit 4 | GFCI | 005 | 漏电流故障 | Leakage current faults | DSP | 外部
|  | bit 5 | OVRT | 006 | 高穿错误 | High penetration error | DSP | 外部
|  | bit 6 | LVRT | 007 | 低穿错误 | Low penetration error | DSP | 外部
|  | bit 7 | IslandFault | 008 | 孤岛错误 | Islanding error | DSP | 外部
| byte 1 | bit 0 | GridOVPInstant1 | 009 | 电网瞬时值过压1 | Grid instantaneous value overvoltage 1 | DSP
|  | bit 1 | GridOVPInstant2 | 010 | 电网瞬时值过压2 | Grid instantaneous value overvoltage 2 | DSP
|  | bit 2 | VGridLineFault | 011 | 电网线电压错误 | Grid line voltage error | DSP | 外部
|  | bit 3 | InvVoltFault | 012 | 逆变电压错误 | Inverter voltage error | DSP
|  | bit 4 | RefluxFault | 013 | 防逆流过载 | Anti-backflow overload | DSP | 外部
|  | bit 5 | VGridUnbalance | 014 | 电网电压不平衡 | Grid voltage unbalance | DSP | 外部
|  | bit 6 | InvOVPInstant | 015 | 逆变瞬时值过压 | Inverter transient overvoltage
|  | bit 7 | GridPhaseMutation | 016 | 电网相变突变 | Sudden grid phase change
Fault2 | byte 0 | bit 0 | HwADErrIGrid | 017 | 电网电流采样错误 | Grid current sampling error | DSP |  | 采样错误
|  | bit 1 | HwADErrDCI(AC) | 018 | DCI采样错误(AC) | DCI sampling error (AC) | DSP
|  | bit 2 | HwADErrVGrid(DC) | 019 | 网压采样错误(DC) | Network voltage sampling error (DC) | DSP
|  | bit 3 | HwADErrVGrid(AC) | 020 | 网压采样错误(AC) | Network voltage sampling error (AC) | DSP
|  | bit 4 | HwGFCIFault(DC) | 021 | GFCI采样错误(DC) | GFCI sampling error (DC) | DSP
|  | bit 5 | HwGFCIFault(AC) | 022 | GFCI采样错误(AC) | GFCI sampling error (AC) | DSP
|  | bit 6 | HwADErrDCV | 023 | DCV采样错误 | DCV sampling error | DSP
|  | bit 7 | HwADErrIdc | 024 | 输入电流采样错误 | Input current sampling error | DSP
| byte 1 | bit 0 | HwADErrDCI(DC) | 025 | DCI采样错误(DC) | DCI sampling error (DC) | DSP
|  | bit 1 | HwADErrIdcBranch | 026 | 支路电流采样错误 | Branch current sampling error | DSP
|  | bit 2 | PVLowImpedance | 027 | PV-对地阻抗低 | PV - low impedance to ground
|  | bit 3 | PIDAbnormalOut | 028 | PID异常输出 | PID abnormal output
|  | bit 4 | ConsistentGFCI | 029 | 漏电流一致性错误 | Leakage current consistency error | DSP
|  | bit 5 | ConsistentVgrid | 030 | 网压一致性错误 | Net voltage consistency error | DSP
|  | bit 6 | ConsistentDCI | 031 | DCI一致性错误 | DCI consistency error | DSP
|  | bit 7 | N-PE fault | 032 | 中性点接地故障 | Neutral ground fault
Fault3 | byte 0 | bit 0 | SpiCommFault(DC) | 033 | SPI通信错误(DC) | SPI communication error (DC) | DSP
|  | bit 1 | SpiCommFault(AC) | 034 | SPI通信错误(AC) | SPI communication error (AC) | DSP
|  | bit 2 | SChip_Fault | 035 | 芯片错误(DC) | Chip error (DC) | DSP
|  | bit 3 | MChip_Fault | 036 | 芯片错误(AC) | Chip error (AC) | DSP
|  | bit 4 | HwAuxPowerFault | 037 | 辅助电源错误 | Auxiliary power error | DSP
|  | bit 5 | InvSoftStartFail | 038 | 逆变软启动失败 | Inverter soft start failure | DSP
|  | bit 6 | ArcShutdownAlarm | 039 | 电弧关机保护 | Arc shutdown protection | DSP | 外部
|  | bit 7 | LowLightChkFail | 040 | 弱光检测失败 | Weak light detection failure | DSP
| byte 1 | bit 0 | RelayFail | 041 | 继电器检测失败 | Relay detection failure | DSP |  | 系统
|  | bit 1 | IsoFault | 042 | 绝缘阻抗低 | Low insulation impedance | DSP | 外部
|  | bit 2 | PEConnectFault | 043 | 接地错误 | Grounding error | DSP | 外部
|  | bit 3 | InputConfigError | 044 | 输入模式设置错误 | Wrong input mode setting | DSP | 外部
|  | bit 4 | CTDisconnect | 045 | CT错误 | CT error | DSP | 外部
|  | bit 5 | ReversalConnect | 046 | 输入反接错误 | Input reversal error | DSP | 外部
|  | bit 6 | ParallelFault | 047 | 并机错误 | Parallel error | DSP | 外部
|  | bit 7 | SNTypeFault | 048 | 序列号错误 | Serial number error | DSP
Fault4 | byte 0 | bit 0 | TempErrBat | 049 | 电池温度保护 | Battery temperature protection | DSP | 外部 | 温度
|  | bit 1 | TempErrHeatSink1 | 050 | 散热器1温度保护 | Heatsink 1 temperature protection | DSP | 外部
|  | bit 2 | TempErrHeatSink2 | 051 | 散热器2温度保护 | Heater 2 temperature protection | DSP | 外部
|  | bit 3 | TempErrHeatSink3 | 052 | 散热器3温度保护 | Heater 3 temperature protection | DSP | 外部
|  | bit 4 | TempErrHeatSink4 | 053 | 散热器4温度保护 | Heatsink 4 temperature protection | DSP | 外部
|  | bit 5 | TempErrHeatSink5 | 054 | 散热器5温度保护 | Radiator 5 temperature protection | DSP | 外部
|  | bit 6 | TempErrHeatSink6 | 055 | 散热器6温度保护 | Radiator 6 temperature protection | DSP | 外部
|  | bit 7 |  | 056
| byte 1 | bit 0 | TempErrEnv1 | 057 | 环境温度1保护 | Ambient temperature 1 protection | DSP | 外部
|  | bit 1 | TempErrEnv2 | 058 | 环境温度2保护 | Ambient temperature 2 protection | DSP | 外部
|  | bit 2 | TempErrInv1 | 059 | 模块1温度保护 | Module 1 temperature protection | DSP | 外部
|  | bit 3 | TempErrInv2 | 060 | 模块2温度保护 | Module 2 temperature protection | DSP | 外部
|  | bit 4 | TempErrInv3 | 061 | 模块3温度保护 | Module 3 temperature protection | DSP | 外部
|  | bit 5 | TempDiffErrInv | 062 | 模块温差过大 | Module temperature difference too large | DSP
|  | bit 6 |  | 063
|  | bit 7 |  | 064
Fault5 | byte 0 | bit 0 | BusRmsUnbalance | 065 | 母线有效值不平衡 | Busbar RMS unbalance | DSP |  | 过欠压
|  | bit 1 | BusInstUnbalance | 066 | 母线瞬时值不平衡 | Busbar instantaneous value unbalance | DSP
|  | bit 2 | BusUVP | 067 | 并网过程母线欠压 | Busbar undervoltage during grid connection | DSP
|  | bit 3 | BusZVP | 068 | 母线低压 | Busbar low voltage | DSP
|  | bit 4 | PVOVP | 069 | PV过压 | PV overvoltage | DSP
|  | bit 5 | BatOVP | 070 | 电池过压 | Battery over-voltage | DSP
|  | bit 6 | LLCBusOVP | 071 | LLCBus过压保护 | LLCBus overvoltage protection | DSP
|  | bit 7 | SwBusRmsOVP | 072 | 母线Rms软件过压 | Busbar Rms software overvoltage | DSP
| byte 1 | bit 0 | SwBusIOVP | 073 | 母线瞬时软件过压 | Busbar Transient Software Overvoltage | DSP
|  | bit 1 | FlyingCapOVP | 074 | 飞跨电容过压保护 | Fly-span capacitor overvoltage protection | DSP
|  | bit 2 | FlyingCapUVP | 075 | 飞跨电容欠压保护 | Fly-span capacitor under-voltage protection | DSP
|  | bit 3 | PVUVP | 076 | PV欠压 | PV undervoltage
|  | bit 4 |  | 077
|  | bit 5 |  | 078
|  | bit 6 |  | 079
|  | bit 7 |  | 080
Fault6 | byte 0 | bit 0 | SwBatOCP | 081 | 电池过流软件保护 | Battery Overcurrent Software Protection | DSP |  | 电流
|  | bit 1 | DciOCP | 082 | Dci过流保护 | Dci overcurrent protection | DSP
|  | bit 2 | SwIOCP | 083 | 输出瞬时电流保护 | Output transient current protection | DSP
|  | bit 3 | SwBuckBoostOCP | 084 | BckBst软件过流 | BckBst software overcurrent | DSP
|  | bit 4 | SwAcRmsOCP | 085 | 逆变Rms电流保护 | Inverter Rms current protection | DSP
|  | bit 5 | SwPvOCPInstant | 086 | PV瞬时软件过流 | PV transient software overcurrent | DSP
|  | bit 6 | IpvUnbalance | 087 | PV并联不均流 | PV parallel uneven current | DSP
|  | bit 7 | IacUnbalance | 088 | 输出电流不平衡 | Output current unbalance | DSP
| byte 1 | bit 0 | SwPvOCP | 089 | PV软件过流保护 | PV software overcurrent protection | DSP
|  | bit 1 | IbalanceOCP | 090 | 平衡电路过流保护 | Balanced circuit overcurrent protection | DSP
|  | bit 2 | ResOver | 091 | 谐振保护 | Resonance protection | DSP
|  | bit 3 | SwAcCBCFault | 092 | 软件逐波限流保护 | Software wave-by-wave current limit protection | DSP
|  | bit 4 | SwPvBranchOCP | 093 | PV支路软件过流（默认使能） | PV branch software overcurrent (enabled by default)
|  | bit 5 |  | 094
|  | bit 6 |  | 095
|  | bit 7 |  | 096
Fault7 | byte 0 | bit 0 | HwLLCBusOVP | 097 | LLC母线硬件过压 | LLC busbar hardware overvoltage | DSP |  | 硬件信号
|  | bit 1 | HwBusOVP | 098 | 逆变母线硬件过压 | Inverter bus hardware overvoltage | DSP
|  | bit 2 | HwBuckBoostOCP | 099 | BckBst硬件过流 | BckBst hardware overcurrent | DSP
|  | bit 3 | HwBatOCP | 100 | 电池硬件过流 | Battery hardware overcurrent | DSP
|  | bit 4 |  | 101
|  | bit 5 | HwPVOCP | 102 | PV硬件过流 | PV hardware overcurrent | DSP
|  | bit 6 | HwACOCP | 103 | 交流输出硬件过流 | AC output hardware overcurrent | DSP
|  | bit 7 | HwDiffOCP | 104 | 硬件差分过流 | Hardware differential overcurrent
| byte 1 | bit 0 | MeterCommFault | 105 | 电表通讯错误 | Meter communication error | DSP | 外部 | 硬件信号预留、过载
|  | bit 1 | SNMachineFault | 106 | 序列号机型错误 | Serial number model error | DSP
|  | bit 2 | HwVerError | 107 | 硬件版本不匹配 | Hardware version mismatch
|  | bit 3 |  | 108
|  | bit 4 |  | 109
|  | bit 5 | Overload1 | 110 | 过载保护1 | Overload protection 1 | DSP | 外部
|  | bit 6 | Overload2 | 111 | 过载保护2 | Overload protection 2 | DSP | 外部
|  | bit 7 | Overload3 | 112 | 过载保护3 | Overload protection 3 | DSP | 外部
Fault8 | byte 0 | bit 0 | OverTempDerating | 113 | 过温降载 | Over-temperature load shedding | DSP | 外部、提示 | 降载 | The fault word is only used to generate an alarm and does not directly put the system into a fault state.
|  | bit 1 | FreqDerating | 114 | 频率降载 | Frequency down load | DSP | 外部、提示
|  | bit 2 | FreqLoading | 115 | 频率加载 | Frequency loading | DSP | 外部、提示
|  | bit 3 | VoltDerating | 116 | 电压降载 | Voltage down load | DSP | 外部、提示
|  | bit 4 | VoltLoading | 117 | 电压加载 | Voltage loading | DSP | 外部、提示
|  | bit 5 | LowTempDerating | 118 | 低温降载 | Low temperature load shedding | DSP
|  | bit 6 |  | 119
|  | bit 7 |  | 120
| byte 1 | bit 0 | SpdFail(DC) | 121 | 防雷故障(DC) | Lightning Protection Fault (DC) | DSP | 外部、提示 | 关机
|  | bit 1 | SpdFail(AC) | 122 | 防雷故障(AC) | Lightning protection (AC) | DSP | 外部、提示
|  | bit 2 |  | 123
|  | bit 3 | BatDchgProhibit | 124 | 电池禁放保护 | Battery lockout protection | DSP | 外部、提示
|  | bit 4 | BatLowVoltShut | 125 | 电池低压关机 | Battery low voltage shutdown | DSP | 外部、提示
|  | bit 5 |  | 126
|  | bit 6 |  | 127
|  | bit 7 |  | 128
Fault9 | byte 0 | bit 0 | PermHwAcOCP | 129 | AC硬件过流故障 | AC hardware overcurrent fault | DSP | 外部 | 永久性
|  | bit 1 | PermBusOVP | 130 | Bus过压故障 | Bus overvoltage fault | DSP | 外部
|  | bit 2 | PermHwBusOVP | 131 | Bus硬件过压故障 | Bus hardware over-voltage fault | DSP | 外部
|  | bit 3 | PermIpvUnbalance | 132 | PV不均流故障 | PV uneven flow fault | DSP | 外部
|  | bit 4 | PermEPSBatOCP | 133 | EPS电池过流故障 | EPS battery overcurrent fault | DSP | 外部
|  | bit 5 | PermAcOCPInstant | 134 | 输出瞬时过流故障 | Output transient overcurrent fault | DSP | 外部
|  | bit 6 | PermIacUnbalance | 135 | AC电流不平衡故障 | AC current unbalance fault | DSP | 外部
|  | bit 7 | PermInvStartFail | 136 | 逆变软启失败故障 | Inverter soft start failure fault
| byte 1 | bit 0 | PermInCfgError | 137 | 输入模式设置故障 | Input mode setting fault | DSP | 外部
|  | bit 1 | PermDCOCPInstant | 138 | 输入过流故障 | Input overcurrent fault | DSP | 外部
|  | bit 2 | PermHwDCOCP | 139 | 输入硬件过流故障 | Input hardware overcurrent fault | DSP | 外部
|  | bit 3 | PermRelayFail | 140 | 继电器永久性故障 | Relay permanent failure | DSP | 外部
|  | bit 4 | PermBusUnbalance | 141 | Bus不平衡故障 | Bus unbalance fault | DSP | 外部
|  | bit 5 | PermSpdFail(DC) | 142 | 防雷故障(DC) | Lightning protection fault (DC) | DSP
|  | bit 6 | PermSpdFail(AC) | 143 | 防雷故障(AC) | Lightning protection fault (AC) | DSP
|  | bit 7 | PermGridRlyFail | 144 | 电网继电器故障 | Grid relay fault
Fault10 | byte 0 | bit 0 | USBFault | 145 | USB故障 | USB fault | ARM |  | 通讯板
|  | bit 1 | WifiFault | 146 | WIFI故障 | WIFI fault | ARM
|  | bit 2 | BluetoothFault | 147 | 蓝牙故障 | Bluetooth fault | ARM
|  | bit 3 | RTCFault | 148 | RTC时钟故障 | RTC clock fault | ARM
|  | bit 4 | CommEEPROMFault | 149 | 通信板EEPROM错误 | Communication board EEPROM error | ARM
|  | bit 5 | FlashFault | 150 | 通信板FLASH错误 | Communication board FLASH error | ARM
|  | bit 6 |  | 151
|  | bit 7 | SafetyVerFault | 152 | 安规版本错误 | Safety version error | ARM | 外部
| byte 1 | bit 0 | SCILose(DC) | 153 | SCI错误(DC) | SCI error (DC) | ARM
|  | bit 1 | SCILose(AC) | 154 | SCI错误(AC) | SCI error (AC) | ARM
|  | bit 2 | SCILose(Fuse) | 155 | SCI错误(Fuse) | SCI error (Fuse) | ARM
|  | bit 3 | SoftVerError | 156 | 软件版本不一致 | Software version inconsistency | ARM | 外部
|  | bit 4 | BMS1CommFault | 157 | 锂电池1通信故障 | Lithium battery 1 communication failure | ARM | 外部
|  | bit 5 | BMS2CommFault | 158 | 锂电池2通信故障 | Lithium battery 2 communication failure | ARM | 外部
|  | bit 6 | BMS3CommFault | 159 | 锂电池3通信故障 | Lithium battery 3 communication failure | ARM | 外部
|  | bit 7 | BMS4CommFault | 160 | 锂电池4通信故障 | Lithium battery 4 communication failure | ARM | 外部
Fault11 | byte 0 | bit 0 | ForceShutdown | 161 | 强制关机 | Forced shutdown | ARM | 外部 | 通讯板关机、降载
|  | bit 1 | RemoteShutdown | 162 | 远程关机 | Remote shutdown | ARM | 外部
|  | bit 2 | Drms0Shutdown | 163 | Drms0关机 | Drms0 shutdown | ARM | 外部
|  | bit 3 | PSCommFault | 164 | 电站通讯故障关机 | Power station communication failure shutdown
|  | bit 4 |  | 165 |  |  | ARM | 外部
|  | bit 5 |  | 166 |  |  | ARM | 外部
|  | bit 6 |  | 167 |  |  | ARM | 外部
|  | bit 7 |  | 168
| byte 1 | bit 0 | FanFault1 | 169 | 风扇1故障 | Fan 1 failure | ARM | 外部 | 外设组件
|  | bit 1 | FanFault2 | 170 | 风扇2故障 | Fan 2 fault | ARM | 外部
|  | bit 2 | FanFault3 | 171 | 风扇3故障 | Fan 3 fault | ARM | 外部
|  | bit 3 | FanFault4 | 172 | 风扇4故障 | Fan 4 fault | ARM | 外部
|  | bit 4 | FanFault5 | 173 | 风扇5故障 | Fan 5 fault | ARM | 外部
|  | bit 5 | FanFault6 | 174 | 风扇6故障 | Fan 6 fault | ARM | 外部
|  | bit 6 | FanFault7 | 175 | 风扇7故障 | Fan 7 fault | ARM | 外部
|  | bit 7 |  | 176 |  |  | ARM | 外部
Fault12 | byte 0 | bit 0 | BMS OVP | 177 | BMS过压保护 | BMS over-voltage protection | BMS | 外部，提示 | BMS
|  | bit 1 | BMS UVP | 178 | BMS欠压保护 | BMS undervoltage protection | BMS | 外部，提示
|  | bit 2 | BMS OTP | 179 | BMS高温保护 | BMS high temperature protection | BMS | 外部，提示
|  | bit 3 | BMS UTP | 180 | BMS低温保护 | BMS low temperature protection | BMS | 外部，提示
|  | bit 4 | BMS OCP | 181 | BMS过流保护 | BMS overcurrent protection | BMS | 外部，提示
|  | bit 5 | BMS Short | 182 | BMS短路保护 | BMS short circuit protection | BMS | 外部，提示
|  | bit 6 | BMS VerFault | 183 | BMS版本不一致 | BMS version inconsistency | ARM | 外部，提示
|  | bit 7 | BMS CAN VerFault | 184 | BMSCAN版本不一致 | BMS CAN version inconsistency | ARM | 外部，提示
| byte 1 | bit 0 | BMS CAN VerLow | 185 | BMS CAN版本过低 | BMS CAN version too low | ARM | 外部，提示
|  | bit 1 | BatDischargeHTP | 186 | 电池放电过温保护 | Battery discharge over-temperature protection
|  | bit 2 | BatDischargeLTP | 187 | 电池放电低温保护 | Battery discharge low temperature protection
|  | bit 3 | BatChargeHTP | 188 | 电池充电过温保护 | Battery charging over-temperature protection
|  | bit 4 | AFCICommLose | 189 | 电弧设备通信故障 | Arc device communication failure | ARM | 外部，提示
|  | bit 5 | BatChargeLTP | 190 | 电池充电低温保护 | Battery charging low temperature protection | ARM
|  | bit 6 | PID_Output_Fail | 191 | PID修复失败 | PID repair failure | ARM
|  | bit 7 | PLC_Com_Fail | 192 | PLC模块心跳丢失 | PLC module heartbeat lost
Fault13 | byte 0 | bit 0 | StrFuseALM1-1 | 193 | 组串保险开路1-1 | String fuse open 1-1 | FUSE |  | FUSE
|  | bit 1 | StrFuseALM1-2 | 194 | 组串保险开路1-2 | String fuse open 1-2 | FUSE
|  | bit 2 | StrFuseALM2-1 | 195 | 组串保险开路2-1 | String fuse open circuit 2-1 | FUSE
|  | bit 3 | StrFuseALM2-2 | 196 | 组串保险开路2-2 | String Fuse Open 2-2 | FUSE
|  | bit 4 | StrFuseALM3-1 | 197 | 组串保险开路3-1 | Serial Fuse Open 3-1 | FUSE
|  | bit 5 | StrFuseALM3-2 | 198 | 组串保险开路3-2 | String Insurance Open 3-2 | FUSE
|  | bit 6 | StrFuseALM4-1 | 199 | 组串保险开路4-1 | String insurance open circuit 4-1 | FUSE
|  | bit 7 | StrFuseALM4-2 | 200 | 组串保险开路4-2 | String Insurance Open 4-2 | FUSE
| byte 1 | bit 0 | StrFuseALM5-1 | 201 | 组串保险开路5-1 | String insurance open circuit 5-1 | FUSE
|  | bit 1 | StrFuseALM5-2 | 202 | 组串保险开路5-2 | String insurance open circuit 5-2 | FUSE
|  | bit 2 | StrFuseALM6-1 | 203 | 组串保险开路6-1 | String insurance open circuit 6-1 | FUSE
|  | bit 3 | StrFuseALM6-2 | 204 | 组串保险开路6-2 | String Insurance Open 6-2 | FUSE
|  | bit 4 | StrFuseALM7-1 | 205 | 组串保险开路7-1 | String insurance open circuit 7-1 | FUSE
|  | bit 5 | StrFuseALM7-2 | 206 | 组串保险开路7-2 | String insurance open 7-2 | FUSE
|  | bit 6 | StrFuseALM8-1 | 207 | 组串保险开路8-1 | String insurance open 8-1 | FUSE
|  | bit 7 | StrFuseALM8-2 | 208 | 组串保险开路8-2 | String insurance open 8-2 | FUSE
Fault14 | byte 0 | bit 0 | StrFuseALM9-1 | 209 | 组串保险开路9-1 | String insurance open circuit 9-1 | FUSE
|  | bit 1 | StrFuseALM9-2 | 210 | 组串保险开路9-2 | String insurance open circuit 9-2 | FUSE
|  | bit 2 | StrFuseALM10-1 | 211 | 组串保险开路10-1 | String insurance open circuit 10-1 | FUSE
|  | bit 3 | StrFuseALM10-2 | 212 | 组串保险开路10-2 | String insurance open circuit 10-2 | FUSE
|  | bit 4 | StrFuseALM11-1 | 213 | 组串保险开路11-1 | String insurance open circuit 11-1 | FUSE
|  | bit 5 | StrFuseALM11-2 | 214 | 组串保险开路11-2 | String insurance open circuit 11-2 | FUSE
|  | bit 6 | StrFuseALM12-1 | 215 | 组串保险开路12-1 | String insurance open circuit 12-1 | FUSE
|  | bit 7 | StrFuseALM12-2 | 216 | 组串保险开路12-2 | String insurance open circuit 12-2 | FUSE
| byte 1 | bit 0 | StrFuseALM13-1 | 217 | 组串保险开路13-1 | String insurance open circuit 13-1 | FUSE
|  | bit 1 | StrFuseALM13-2 | 218 | 组串保险开路13-2 | String insurance open circuit 13-2 | FUSE
|  | bit 2 | StrFuseALM14-1 | 219 | 组串保险开路14-1 | String insurance open circuit 14-1 | FUSE
|  | bit 3 | StrFuseALM14-2 | 220 | 组串保险开路14-2 | String insurance open circuit 14-2 | FUSE
|  | bit 4 | StrFuseALM15-1 | 221 | 组串保险开路15-1 | String insurance open circuit 15-1 | FUSE
|  | bit 5 | StrFuseALM15-2 | 222 | 组串保险开路15-2 | String insurance open circuit 15-2 | FUSE
|  | bit 6 | StrFuseALM16-1 | 223 | 组串保险开路16-1 | String insurance open circuit 16-1 | FUSE
|  | bit 7 | StrFuseALM16-2 | 224 | 组串保险开路16-2 | String fuse open 16-2 | FUSE
Fault15 | byte 0 | bit 0 | InputFuseALM0 | 225 | 输入保险开路0 | Input fuse open 0 | FUSE
|  | bit 1 | InputFuseALM1 | 226 | 输入保险开路1 | Input fuse open 1 | FUSE
|  | bit 2 | InputFuseALM2 | 227 | 输入保险开路2 | Input fuse open 2 | FUSE
|  | bit 3 | InputFuseALM3 | 228 | 输入保险开路3 | Input fuse open 3 | FUSE
|  | bit 4 | InputFuseALM4 | 229 | 输入保险开路4 | Input fuse open 4 | FUSE
|  | bit 5 | InputFuseALM5 | 230 | 输入保险开路5 | Input fuse open 5 | FUSE
|  | bit 6 | InputFuseALM6 | 231 | 输入保险开路6 | Input insurance open circuit 6 | FUSE
|  | bit 7 | InputFuseALM7 | 232 | 输入保险开路7 | Input insurance open circuit 7 | FUSE
| byte 1 | bit 0 | InputFuseALM8 | 233 | 输入保险开路8 | Input insurance open circuit 8 | FUSE
|  | bit 1 | InputFuseALM9 | 234 | 输入保险开路9 | Input insurance open circuit 9 | FUSE
|  | bit 2 | InputFuseALM10 | 235 | 输入保险开路10 | Input insurance open circuit 10 | FUSE
|  | bit 3 | InputFuseALM11 | 236 | 输入保险开路11 | Input insurance open circuit 11 | FUSE
|  | bit 4 | InputFuseALM12 | 237 | 输入保险开路12 | Input insurance open circuit 12 | FUSE
|  | bit 5 | InputFuseALM13 | 238 | 输入保险开路13 | Input insurance open circuit13 | FUSE
|  | bit 6 | InputFuseALM14 | 239 | 输入保险开路14 | Input insurance open circuit 14 | FUSE
|  | bit 7 | InputFuseALM15 | 240 | 输入保险开路15 | Input insurance open circuit 15 | FUSE
Fault16 | byte 0 | bit 0 | CombinerOVGp1 | 241 |  |  |  |  | 汇流
|  | bit 1 | CombinerOVGp2 | 242
|  | bit 2 | CombinerOVGp3 | 243
|  | bit 3 | CombinerOVGp4 | 244
|  | bit 4 | CombinerOVGp5 | 245
|  | bit 5 | CombinerOVGp6 | 246
|  | bit 6 | CombinerOVGp7 | 247
|  | bit 7 | CombinerOVGp8 | 248
| byte 1 | bit 0 | CombinerOVGp9 | 249
|  | bit 1 | CombinerOVGp10 | 250
|  | bit 2 | CombinerOVGp11 | 251
|  | bit 3 | CombinerOVGp12 | 252
|  | bit 4 | CombinerOVGp13 | 253
|  | bit 5 | CombinerOVGp14 | 254
|  | bit 6 | CombinerOVGp15 | 255
|  | bit 7 | CombinerOVGp16 | 256
Fault17 | byte 0 | bit 0 | CombinerUVGp1 | 257 |  |  |  |  | 汇流
|  | bit 1 | CombinerUVGp2 | 258
|  | bit 2 | CombinerUVGp3 | 259
|  | bit 3 | CombinerUVGp4 | 260
|  | bit 4 | CombinerUVGp5 | 261
|  | bit 5 | CombinerUVGp6 | 262
|  | bit 6 | CombinerUVGp7 | 263
|  | bit 7 | CombinerUVGp8 | 264
| byte 1 | bit 0 | CombinerUVGp9 | 265
|  | bit 1 | CombinerUVGp10 | 266
|  | bit 2 | CombinerUVGp11 | 267
|  | bit 3 | CombinerUVGp12 | 268
|  | bit 4 | CombinerUVGp13 | 269
|  | bit 5 | CombinerUVGp14 | 270
|  | bit 6 | CombinerUVGp15 | 271
|  | bit 7 | CombinerUVGp16 | 272
Fault18 | byte 0 | bit 0 | CombinerOC1 | 273 |  |  |  |  | 汇流
|  | bit 1 | CombinerOC2 | 274
|  | bit 2 | CombinerOC3 | 275
|  | bit 3 | CombinerOC4 | 276
|  | bit 4 | CombinerOC5 | 277
|  | bit 5 | CombinerOC6 | 278
|  | bit 6 | CombinerOC7 | 279
|  | bit 7 | CombinerOC8 | 280
| byte 1 | bit 0 | CombinerOC9 | 281
|  | bit 1 | CombinerOC10 | 282
|  | bit 2 | CombinerOC11 | 283
|  | bit 3 | CombinerOC12 | 284
|  | bit 4 | CombinerOC13 | 285
|  | bit 5 | CombinerOC14 | 286
|  | bit 6 | CombinerOC15 | 287
|  | bit 7 | CombinerOC16 | 288
Fault19 | byte 0 | bit 0 | CombinerOC17 | 289 |  |  |  |  | 汇流
|  | bit 1 | CombinerOC18 | 290
|  | bit 2 | CombinerOC19 | 291
|  | bit 3 | CombinerOC20 | 292
|  | bit 4 | CombinerOC21 | 293
|  | bit 5 | CombinerOC22 | 294
|  | bit 6 | CombinerOC23 | 295
|  | bit 7 | CombinerOC24 | 296
| byte 1 | bit 0 | CombinerOC25 | 297
|  | bit 1 | CombinerOC26 | 298
|  | bit 2 | CombinerOC27 | 299
|  | bit 3 | CombinerOC28 | 300
|  | bit 4 | CombinerOC29 | 301
|  | bit 5 | CombinerOC30 | 302
|  | bit 6 | CombinerOC31 | 303
|  | bit 7 | CombinerOC32 | 304
Fault20 | byte 0 | bit 0 |  | 305 |  |  |  |  | 汇流
|  | bit 1 |  | 306
|  | bit 2 |  | 307
|  | bit 3 |  | 308
|  | bit 4 |  | 309
|  | bit 5 |  | 310
|  | bit 6 |  | 311
|  | bit 7 |  | 312
| byte 1 | bit 0 |  | 313
|  | bit 1 |  | 314
|  | bit 2 |  | 315
|  | bit 3 |  | 316
|  | bit 4 |  | 317
|  | bit 5 |  | 318
|  | bit 6 |  | 319
|  | bit 7 |  | 320
Fault21 | byte 0 | bit 0 |  | 321 |  |  |  |  | 汇流
|  | bit 1 |  | 322
|  | bit 2 |  | 323
|  | bit 3 |  | 324
|  | bit 4 |  | 325
|  | bit 5 |  | 326
|  | bit 6 |  | 327
|  | bit 7 |  | 328
| byte 1 | bit 0 |  | 329
|  | bit 1 |  | 330
|  | bit 2 |  | 331
|  | bit 3 |  | 332
|  | bit 4 |  | 333
|  | bit 5 |  | 334
|  | bit 6 |  | 335
|  | bit 7 |  | 336
Fault22 | byte 0 | bit 0 | CombinerRefluxFault1 | 337 |  |  |  |  | 汇流
|  | bit 1 | CombinerRefluxFault2 | 338
|  | bit 2 | CombinerRefluxFault3 | 339
|  | bit 3 | CombinerRefluxFault4 | 340
|  | bit 4 | CombinerRefluxFault5 | 341
|  | bit 5 | CombinerRefluxFault6 | 342
|  | bit 6 | CombinerRefluxFault7 | 343
|  | bit 7 | CombinerRefluxFault8 | 344
| byte 1 | bit 0 | CombinerRefluxFault9 | 345
|  | bit 1 | CombinerRefluxFault10 | 346
|  | bit 2 | CombinerRefluxFault11 | 347
|  | bit 3 | CombinerRefluxFault12 | 348
|  | bit 4 | CombinerRefluxFault13 | 349
|  | bit 5 | CombinerRefluxFault14 | 350
|  | bit 6 | CombinerRefluxFault15 | 351
|  | bit 7 | CombinerRefluxFault16 | 352
Fault23 | byte 0 | bit 0 | CombinerRefluxFault17 | 353 |  |  |  |  | 汇流
|  | bit 1 | CombinerRefluxFault18 | 354
|  | bit 2 | CombinerRefluxFault19 | 355
|  | bit 3 | CombinerRefluxFault20 | 356
|  | bit 4 | CombinerRefluxFault21 | 357
|  | bit 5 | CombinerRefluxFault22 | 358
|  | bit 6 | CombinerRefluxFault23 | 359
|  | bit 7 | CombinerRefluxFault24 | 360
| byte 1 | bit 0 | CombinerRefluxFault25 | 361
|  | bit 1 | CombinerRefluxFault26 | 362
|  | bit 2 | CombinerRefluxFault27 | 363
|  | bit 3 | CombinerRefluxFault28 | 364
|  | bit 4 | CombinerRefluxFault29 | 365
|  | bit 5 | CombinerRefluxFault30 | 366
|  | bit 6 | CombinerRefluxFault31 | 367
|  | bit 7 | CombinerRefluxFault32 | 368
Fault24 | byte 0 | bit 0 |  | 369 |  |  |  |  | 汇流
|  | bit 1 |  | 370
|  | bit 2 |  | 371
|  | bit 3 |  | 372
|  | bit 4 |  | 373
|  | bit 5 |  | 374
|  | bit 6 |  | 375
|  | bit 7 |  | 376
| byte 1 | bit 0 |  | 377
|  | bit 1 |  | 378
|  | bit 2 |  | 379
|  | bit 3 |  | 380
|  | bit 4 |  | 381
|  | bit 5 |  | 382
|  | bit 6 |  | 383
|  | bit 7 |  | 384
Fault25 | byte 0 | bit 0 |  | 385 |  |  |  |  | 汇流
|  | bit 1 |  | 386
|  | bit 2 |  | 387
|  | bit 3 |  | 388
|  | bit 4 |  | 389
|  | bit 5 |  | 390
|  | bit 6 |  | 391
|  | bit 7 |  | 392
| byte 1 | bit 0 |  | 393
|  | bit 1 |  | 394
|  | bit 2 |  | 395
|  | bit 3 |  | 396
|  | bit 4 |  | 397
|  | bit 5 |  | 398
|  | bit 6 |  | 399
|  | bit 7 |  | 400
Fault26 | byte 0 | bit 0 | AFCI0 | 401 | 拉弧故障 |  |  |  | 拉弧
|  | bit 1 | AFCI1 | 402 | 拉弧故障
|  | bit 2 | AFCI2 | 403 | 拉弧故障
|  | bit 3 | AFCI3 | 404 | 拉弧故障
|  | bit 4 | AFCI4 | 405 | 拉弧故障
|  | bit 5 | AFCI5 | 406 | 拉弧故障
|  | bit 6 | AFCI6 | 407 | 拉弧故障
|  | bit 7 | AFCI7 | 408 | 拉弧故障
| byte 1 | bit 0 | AFCI8 | 409 | 拉弧故障
|  | bit 1 | AFCI9 | 410 | 拉弧故障
|  | bit 2 | AFCI10 | 411 | 拉弧故障
|  | bit 3 | AFCI11 | 412 | 拉弧故障
|  | bit 4 | AFCI12 | 413 | 拉弧故障
|  | bit 5 | AFCI13 | 414 | 拉弧故障
|  | bit 6 | AFCI14 | 415 | 拉弧故障
|  | bit 7 | AFCI15 | 416 | 拉弧故障
Fault27 | byte 0 | bit 0 | AFCI16 | 417 | 拉弧故障 |  |  |  | 拉弧
|  | bit 1 | AFCI17 | 418 | 拉弧故障
|  | bit 2 | AFCI18 | 419 | 拉弧故障
|  | bit 3 | AFCI19 | 420 | 拉弧故障
|  | bit 4 | AFCI20 | 421 | 拉弧故障
|  | bit 5 | AFCI21 | 422 | 拉弧故障
|  | bit 6 | AFCI22 | 423 | 拉弧故障
|  | bit 7 | AFCI23 | 424 | 拉弧故障
| byte 1 | bit 0 | AFCI24 | 425 | 拉弧故障
|  | bit 1 | AFCI25 | 426 | 拉弧故障
|  | bit 2 | AFCI26 | 427 | 拉弧故障
|  | bit 3 | AFCI27 | 428 | 拉弧故障
|  | bit 4 | AFCI28 | 429 | 拉弧故障
|  | bit 5 | AFCI29 | 430 | 拉弧故障
|  | bit 6 | AFCI30 | 431 | 拉弧故障
|  | bit 7 | AFCI31 | 432 | 拉弧故障
Fault28 | byte 0 | bit 0 |  | 433 |  |  | Protocol version error(ARM) |  | 协议版本错误(ARM)
|  | bit 1 |  | 434
|  | bit 2 |  | 435
|  | bit 3 |  | 436
|  | bit 4 |  | 437
|  | bit 5 |  | 438
|  | bit 6 |  | 439
|  | bit 7 |  | 440
| byte 1 | bit 0 | ModifyOVP | 441 | 设置过压保护事件
|  | bit 1 |  | 442
|  | bit 2 |  | 443
|  | bit 3 |  | 444
|  | bit 4 |  | 445
|  | bit 5 |  | 446
|  | bit 6 |  | 447
|  | bit 7 |  | 448
Fault29 | byte 0 | bit 0 | VGridNPEOver | 449 | 零地电压过高 |  | Electricity network |  | 电网
|  | bit 1 | SwPvBranchOCP | 450 | PV支路软件过流（默认不使能）
|  | bit 2 |  | 451
|  | bit 3 |  | 452
|  | bit 4 |  | 453
|  | bit 5 |  | 454
|  | bit 6 |  | 455
|  | bit 7 |  | 456
| byte 1 | bit 0 |  | 457
|  | bit 1 |  | 458
|  | bit 2 |  | 459
|  | bit 3 |  | 460
|  | bit 4 |  | 461
|  | bit 5 |  | 462
|  | bit 6 |  | 463
|  | bit 7 | Disable | 464 | 该位禁用
Fault30 | byte 0 | bit 0 |  | 465 |  |  | Electricity network |  | 电网
|  | bit 1 |  | 466
|  | bit 2 |  | 467
|  | bit 3 |  | 468
|  | bit 4 |  | 469
|  | bit 5 |  | 470
|  | bit 6 |  | 471
|  | bit 7 |  | 472
| byte 1 | bit 0 |  | 473
|  | bit 1 |  | 474
|  | bit 2 |  | 475
|  | bit 3 |  | 476
|  | bit 4 |  | 477
|  | bit 5 |  | 478
|  | bit 6 |  | 479
|  | bit 7 | Disable | 480 | 该位禁用

## Status information sheet
Table | Byte | Bit | 位字段 | 编号 | 备注 | Remarks
State1 | byte 0 | bit 0 | GridUVDerating | 001 | 电网低压降载（逆变器机型根据输出最大电流*电网最低相电压得出的降载功率） | Grid low voltage load shedding (load shedding power for inverter models based on maximum output current * lowest grid phase voltage)
|  | bit 1 | OverTempDerating | 002 | 过温降载 | Over-temperature load shedding
|  | bit 2 | BusOVDerating | 003 | 母线过压降载 | Busbar overvoltage load shedding
|  | bit 3 | QLimitedP | 004 | 无功限有功 | reactive power limited active power
|  | bit 4 | CmdPDerating | 005 | 指令有功降载（安规） | Commanded active load shedding (safety regulations)
|  | bit 5 | DRMsDerating | 006 | DRMs降载 | DRMs load shedding
|  | bit 6 | FeedInLimitation | 007 | 防逆流降载 | Anti-reflux load shedding
|  | bit 7 | RemotePCtrl | 008 | 远程有功控制（通信箱） | Remote active control (communication box)
| byte 1 | bit 0 | OVUVDerating | 009 | 电网过欠压安规降载 (安规的电网过欠压降载) | Grid over-undervoltage safety regulation load shedding (grid over-undervoltage load shedding for safety regulation)
|  | bit 1 | OFDerating | 010 | 过频降载 | Over-frequency load shedding
|  | bit 2 | UFLoading | 011 | 欠频加载 | Under-frequency loading
|  | bit 3 | InnerDerating | 012 | 内部(其他)降载（调制比/升压比降载） | Internal (other) load shedding (modulation ratio/boost ratio load shedding)
|  | bit 4 |  | 013
|  | bit 5 |  | 014
|  | bit 6 |  | 015
|  | bit 7 |  | 016
State2 | byte 0 | bit 0 | RemotePFCtrl | 017 | 远程PF控制 | Remote PF control
|  | bit 1 | RemoteQCtrl | 018 | 远程无功(无功百分比)控制 | Remote reactive power (reactive power percentage) control
|  | bit 2 | IndependenceQCtrl | 019 | 独立无功控制 | Independent reactive power control
|  | bit 3 |  | 020
|  | bit 4 |  | 021
|  | bit 5 |  | 022
|  | bit 6 |  | 023
|  | bit 7 |  | 024
| 0 | bit 0 | ForceOff | 025 | 强制关机（二代机独有，三代光伏预留的功能接口） | Forced shutdown (unique to 2nd generation machines, functional interface reserved for 3rd generation PV)
|  | bit 1 | RemoteOff | 026 | 远程关机 (上位机） | Remote shutdown (upconverter)
|  | bit 2 | DRMs0Off | 027 | DRMs0关机 | DRMs0 shutdown
|  | bit 3 |  | 028
|  | bit 4 |  | 029
|  | bit 5 |  | 030
|  | bit 6 |  | 031
|  | bit 7 |  | 032
State3 | byte 0 | bit 0 |  | 033
|  | bit 1 |  | 034
|  | bit 2 |  | 035
|  | bit 3 |  | 036
|  | bit 4 |  | 037
|  | bit 5 |  | 038
|  | bit 6 |  | 039
|  | bit 7 |  | 040
| byte 1 | bit 0 |  | 041
|  | bit 1 |  | 042
|  | bit 2 |  | 043
|  | bit 3 |  | 044
|  | bit 4 |  | 045
|  | bit 5 |  | 046
|  | bit 6 |  | 047
|  | bit 7 |  | 048
State4 | byte 0 | bit 0 |  | 049
|  | bit 1 |  | 050
|  | bit 2 |  | 051
|  | bit 3 |  | 052
|  | bit 4 |  | 053
|  | bit 5 |  | 054
|  | bit 6 |  | 055
|  | bit 7 |  | 056
| byte 1 | bit 0 |  | 057
|  | bit 1 |  | 058
|  | bit 2 |  | 059
|  | bit 3 |  | 060
|  | bit 4 |  | 061
|  | bit 5 |  | 062
|  | bit 6 |  | 063
|  | bit 7 |  | 064
State5 | byte 0 | bit 0 |  | 065
|  | bit 1 |  | 066
|  | bit 2 |  | 067
|  | bit 3 |  | 068
|  | bit 4 |  | 069
|  | bit 5 |  | 070
|  | bit 6 |  | 071
|  | bit 7 |  | 072
| byte 1 | bit 0 |  | 073
|  | bit 1 |  | 074
|  | bit 2 |  | 075
|  | bit 3 |  | 076
|  | bit 4 |  | 077
|  | bit 5 |  | 078
|  | bit 6 |  | 079
|  | bit 7 |  | 080
State6 | byte 0 | bit 0 | RemoteDeratingEnable | 081 | 远程降载使能
|  | bit 1 | LogicIfDeratingEnable | 082 | 逻辑接口降载使能
|  | bit 2 | FeedInLimitationEnable | 083 | 防逆流降载使能
|  | bit 3 |  | 084
|  | bit 4 |  | 085
|  | bit 5 |  | 086
|  | bit 6 |  | 087
|  | bit 7 |  | 088
| byte 1 | bit 0 |  | 089
|  | bit 1 |  | 090
|  | bit 2 |  | 091
|  | bit 3 |  | 092
|  | bit 4 |  | 093
|  | bit 5 |  | 094
|  | bit 6 |  | 095
|  | bit 7 |  | 096
State7 | byte 0 | bit 0 |  | 097
|  | bit 1 |  | 098
|  | bit 2 |  | 099
|  | bit 3 |  | 100
|  | bit 4 |  | 101
|  | bit 5 |  | 102
|  | bit 6 |  | 103
|  | bit 7 |  | 104
| byte 1 | bit 0 |  | 105
|  | bit 1 |  | 106
|  | bit 2 |  | 107
|  | bit 3 |  | 108
|  | bit 4 |  | 109
|  | bit 5 |  | 110
|  | bit 6 |  | 111
|  | bit 7 |  | 112
State8 | byte 0 | bit 0 |  | 113
|  | bit 1 |  | 114
|  | bit 2 |  | 115
|  | bit 3 |  | 116
|  | bit 4 |  | 117
|  | bit 5 |  | 118
|  | bit 6 |  | 119
|  | bit 7 |  | 120
| byte 1 | bit 0 |  | 121
|  | bit 1 |  | 122
|  | bit 2 |  | 123
|  | bit 3 |  | 124
|  | bit 4 |  | 125
|  | bit 5 |  | 126
|  | bit 6 |  | 127
|  | bit 7 |  | 128
State9 | byte 0 | bit 0 |  | 129
|  | bit 1 |  | 130
|  | bit 2 |  | 131
|  | bit 3 |  | 132
|  | bit 4 |  | 133
|  | bit 5 |  | 134
|  | bit 6 |  | 135
|  | bit 7 |  | 136
| byte 1 | bit 0 |  | 137
|  | bit 1 |  | 138
|  | bit 2 |  | 139
|  | bit 3 |  | 140
|  | bit 4 |  | 141
|  | bit 5 |  | 142
|  | bit 6 |  | 143
|  | bit 7 |  | 144

## PCU Fault Bit Description
Warning1 (0x6024) | bit | ID | 故障(Fault) | 注释 | Remarks
| 0 | 800
| 1 | 801 | IschgSoftStartFail | 充电软起动失败 | Charge soft start failure
| 2 | 802 | IsdchgSoftStartFail | 放电软起失败 | Discharge soft start failure
| 3 | 803 | Fan1Fault | 风扇1故障 | Fan 1 failure
| 4 | 804 | Fan2Fault | 风扇2故障 | Fan 2 failure
| 5 | 805 | Fan3Fault | 风扇3故障 | Fan 3 failure
| 6 | 806 | Fan4Fault | 风扇4故障 | Fan 4 failure
| 7 | 807 | PCU VerFault | PCU版本不一致 | PCU version inconsistent
| 8 | 808 | HS1HighTempWarning | 散热器1过温告警 | Heatsink 1 overtemperature alarm
| 9 | 809 | EnvHighTempWarning | 环境温度过温告警 | Ambient temperature overtemperature alarm
| 10 | 810 | HS2HighTempWarning | 散热器2过温告警 | Heatsink 2 overtemperature alarm
| 11 | 811
| 12 | 812
| 13 | 813 | StopChgWarning | 禁止充电告警 | Prohibit charging alarm
| 14 | 814 | StopDchgWarning | 禁止放电告警 | Prohibit discharge alarm
| 15 | 815 | BatUnbalancedWarning | 电池不均衡告警 | Battery unbalance alarm
Warning2 (0x6025) | 0 | 816 | BusAvgOVWarning | 母线过压告警 | Bus over-voltage alarm
| 1 | 817 | BusAvgUVWarning | 母线欠压告警 | Bus undervoltage alarm
| 2 | 818 | BatAvgOVWarning | 电池过压告警 | Battery over-voltage alarm
| 3 | 819 | BatAvgUVWarning | 电池欠压告警 | Battery undervoltage alarm
| 4 | 820
| 5 | 821
| 6 | 822
| 7 | 823
| 8 | 824
| 9 | 825
| 11 | 827
| 12 | 828
| 13 | 829
| 14 | 830
| 15 | 831
Warning3 (0x6026) | 0 | 832
| 1 | 833
| 2 | 834
| 3 | 835
| 4 | 836
| 5 | 837
| 6 | 838
| 7 | 839
| 8 | 840
| 9 | 841
| 10 | 842
| 11 | 843
| 12 | 844
| 13 | 845
Warning4 (0x6027) | 0 | 848
| 1 | 849
| 2 | 850
| 3 | 851
| 4 | 852
| 5 | 853
| 6 | 854
| 7 | 855
| 8 | 856
| 9 | 857
| 10 | 858
| 11 | 859
| 12 | 860
| 13 | 861
| 14 | 862
| 15 | 863
Fault1 (0x6028) | 0 | 864 | HS1OverTempFault | 散热器1过温保护 | Heatsink 1 overtemperature protection
| 1 | 865 | OverTempFault_Env | 环境温度过温保护 | Ambient temperature overtemperature protection
| 2 | 866 | SciCommFault | Sci通信故障 | Sci communication fault
| 3 | 867 | Can1CommFault | Can1通信故障 | Can1 communication fault
| 4 | 868 | Relay1Fail | 继电器1故障 | Relay 1 fault
| 5 | 869 | HS2OverTempFault | 散热器2过温保护 | Radiator 2 overtemperature protection
| 6 | 870 | Can2CommFault | Can2通信故障 | Can2 communication fault
| 7 | 871 | Relay2Fail | 继电器2故障 | Relay 2 fault
| 8 | 872 | SwBusInstantOVP | 母线软件过压 | Busbar software over-voltage
| 9 | 873 | SwBusInstantUVP | 母线软件欠压 | Bus software undervoltage
| 10 | 874 | SwBatInstantOVP | 电池软件过压 | Battery software overvoltage
| 11 | 875 | SwBatInstantUVP | 电池软件欠压 | Battery software undervoltage
| 12 | 876 | SwBatInstantOCP | 电池软件过流 | Battery software overcurrent
| 13 | 877 | FlyingCap1OVP | 飞跨电容1过压 | Fly span capacitor 1 overvoltage
| 14 | 878 | FlyingCap2OVP | 飞跨电容2过压 | Fly span capacitor 2 overvoltage
| 15 | 879 | HwOCP | 硬件过流 | Hardware overcurrent
Fault2 (0x6029) | 0 | 880 | unrecoverBusAvgOV | 永久母线过压 | Permanent busbar overvoltage
| 1 | 881 | unrecoverBatAvgUV | 永久电池欠压 | Permanent battery undervoltage
| 2 | 882 | unrecoverOCPInstant | 永久过流 | Permanent overcurrent
| 3 | 883 | unrecoverHwOCP | 永久硬件过流 | Permanent hardware overcurrent
| 4 | 884 | FlyingCap3OVP | 飞跨电容3过压 | Fly span capacitor 3 overvoltage
| 5 | 885 | FlyingCap4OVP | 飞跨电容4过压 | Fly-span capacitor 4 overvoltage
| 6 | 886 | FlyingCap1UVP | 飞跨电容1欠压 | Fly-through capacitor 1 undervoltage
| 7 | 887 | FlyingCap2UVP | 飞跨电容2欠压 | Fly-span capacitor 2 undervoltage
| 8 | 888 | unrecoverRelay1Fail | 继电器1永久故障 | Relay 1 permanently faulty
| 9 | 889 | unrecoverRelay2Fail | 继电器2永久故障 | Relay 2 permanently faulty
| 10 | 890 | FlyingCap3UVP | 飞跨电容3欠压 | Fly-span capacitor 3 undervoltage
| 11 | 891 | FlyingCap4UVP | 飞跨电容4欠压 | Fly-span capacitor 4 undervoltage
| 12 | 892
| 13 | 893 | unrecoverBusSCP | 永久短路保护 | Permanent short circuit protection
| 14 | 894 | unrecoverBatActFail | 永久电池激活失败 | Permanent battery activation failure
| 15 | 895 | unrecoverBusRPP | 永久性BUS反接 | Permanent BUS reverse connection
Fault3 (0x602A) | 0 | 896 | BatteryStateErr | 电池状态错误 | Battery status error
| 1 | 897 | PWMModeErr | PWM模式错误 | PWM mode error
| 2 | 898 | BMSVerionErr | BMS版本错误 | BMS version error
| 3 | 899 | BMSOVOCP | BMS过压过流故障 | BMS overvoltage and overcurrent failure
| 4 | 900 | SwBatAvgOCP | 电池平均值过流保护 | Battery average overcurrent protection
| 5 | 901 | SwAvgOverloadP | 平均值过载保护 | Average value overload protection
| 6 | 902 | SwBusInstantOCP | 母线软件过流 | Busbar software overcurrent
| 7 | 903 | SwCBCOCP | 软件CBC过流保护 | Software CBC overcurrent protection
| 8 | 904 | PackIDErr | PackID 错误 | PackID error
| 9 | 905 | BusSCP | 启机短路保护 | Start-up short circuit protection
| 10 | 906 | SwBusAvgUVP | 母线平均值欠压 | Bus average undervoltage
| 11 | 907 | Clockfail | 时钟故障 | Clock fault
| 12 | 908 | PCSCanCommFault | PCS通信故障 | PCS communication fault
| 13 | 909
| 14 | 910
| 15 | 911
Fault4 (0x602B) | 0 | 912
| 1 | 913
| 2 | 914
| 3 | 915
| 4 | 916
| 5 | 917
| 6 | 918
| 7 | 919
| 8 | 920
| 9 | 921
| 10 | 922
| 11 | 923
| 12 | 924
| 13 | 925
| 14 | 926
| 15 | 927

## BDU fault information
Fault1 | bit | ID | Fault | Note
| 0 | 928 | Reverse battery connection
| 1 | 929 | Fuse failure
| 2 | 930
| 3 | 931
| 4 | 932
| 5 | 933
| 6 | 934
| 7 | 935
| 8 | 936
| 9 | 937
| 10 | 938
| 11 | 939
| 12 | 940
| 13 | 941
| 14 | 942
| 15 | 943

## DCDC Fault Bit Description
fault1 | bit | ID | FAULT | 注释 | Note
| 0 | 600 | LowBusUVP | 低压侧欠压 | Low side undervoltage
| 1 | 601 | SwLowBusOVP | 低压侧过压软件 | Low side overvoltage software
| 2 | 602 | HighBusUVP | 高压侧欠压 | High side undervoltage
| 3 | 603 | SwHighBusOVP | 高压侧过压软件 | High voltage side overvoltage software
| 4 | 604 | FlyCapUnbalanceP | 飞跨电容不平衡 | Fly-through capacitor unbalance
| 5 | 605 | SwLowBusOCP | 低压侧过流软件 | Low voltage side overcurrent software
| 6 | 606 | HwArmChipErr | ARM芯片故障 | ARM chip fault
| 7 | 607 | HwHVPolarityErr | 高压反接故障 | High voltage reverse connection fault
| 8 | 608 | HwHighBusOVP | 高压侧过压硬件 | High voltage side overvoltage hardware
| 9 | 609 | HwLowBusOVP | 低压侧过压硬件 | Low side overvoltage hardware
| 10 | 610 | HwLowBusOCP | 低压侧过流硬件 | Low voltage side overcurrent hardware
| 11 | 611 | HwIGBTDrvErr | IGBT驱动故障 | IGBT driver failure
| 12 | 612 | HwVersionErr | 应急版本号错误 | Emergency version number error
| 13 | 613 | IsoFault | 绝缘故障 | Insulation fault
| 14 | 614 | PEConnectFault | 接地故障 | Ground fault
| 15 | 615 | RelayFail | 继电器故障 | Relay fault
fault2 | 0 | 616 | ArmCommFault | ARM通信故障 | ARM communication fault
| 1 | 617 | PcsCommFault | PCS通信故障 | PCS communication fault
| 2 | 618 | Pcu1CommFault | PCU1通信故障 | PCU1 communication fault
| 3 | 619 | Pcu2CommFault | PCU2通信故障 | PCU2 communication fault
| 4 | 620 | Pcu3CommFault | PCU3通信故障 | PCU3 communication fault
| 5 | 621 | Bms1CommFault | BMS1通信故障 | BMS1 communication fault
| 6 | 622 | Bms2CommFault | BMS2通信故障 | BMS2 communication fault
| 7 | 623 | Bms3CommFault | BMS3通信故障 | BMS3 communication fault
| 8 | 624 | DC1CommFault | DC1通信故障 | DC1 communication fault
| 9 | 625 | DC2CommFault | DC2通信故障 | DC2 communication fault
| 10 | 626 | DC3CommFault | DC3通信故障 | DC3 communication fault
| 11 | 627 | DC4CommFault | DC4通信故障 | DC4 communication fault
| 12 | 628 | DC5CommFault | DC5通信故障 | DC5 communication fault
| 13 | 629 | DC6CommFault | DC6通信故障 | DC6 communication fault
| 14 | 630 | ModuleOTP | 模块过温 | Module over temperature
| 15 | 631 | HwADZerodrift | 零飘 | Zero drift
fault3 | 0 | 632 | HwHvFuseFault | 高压熔丝故障 | High voltage fuse fault
| 1 | 633 | LvSideWakeUpFail | 低压侧唤醒故障 | Low voltage side wake-up fault
| 2 | 634 | LvSideVakeUpTout | 低压侧唤醒超时 | Low voltage side wake-up timeout
| 3 | 635
| 4 | 636
| 5 | 637
| 6 | 638
| 7 | 639
| 8 | 640
| 9 | 641
| 10 | 642
| 11 | 643
| 12 | 644
| 13 | 645
fault4 | 0 | 646
| 1 | 647
| 2 | 648
| 3 | 649
| 4 | 650
| 5 | 651
| 6 | 652
| 7 | 653
| 8 | 654
| 9 | 655
| 10 | 656
| 11 | 657
| 12 | 658
| 13 | 659
| 14 | 660
| 15 | 661
Fault5 | 0 | 662
| 1 | 663
| 2 | 664
| 3 | 665
| 4 | 666
| 5 | 667
| 6 | 668
| 7 | 669
| 8 | 670
| 9 | 671
| 10 | 672
| 11 | 673
| 12 | 674
| 13 | 675
| 14 | 676
| 15 | 677
Fault6 | 0 | 678
| 1 | 679
| 2 | 680
| 3 | 681
| 4 | 682
| 5 | 683
| 6 | 684
| 7 | 685
| 8 | 686
| 9 | 687
| 10 | 688
| 11 | 689
| 12 | 690
| 13 | 691
| 14 | 692
| 15 | 693
| 13 | 694
| 14 | 695
| 15 | 696
Fault7 | 0 | 697
| 1 | 698
| 2 | 699
| 3 | 700
| 4 | 701
| 5 | 702
| 6 | 703
| 7 | 704
| 8 | 705
| 9 | 706
| 10 | 707
| 11 | 708
| 12 | 709
| 13 | 710
| 14 | 711
| 15 | 712
Fault8 | 0 | 713
| 1 | 714
| 2 | 715
| 3 | 716
| 4 | 717
| 5 | 718
| 6 | 719
| 7 | 720
| 8 | 721
| 9 | 722
| 10 | 723
| 11 | 724
| 12 | 725
| 13 | 726
| 14 | 727
| 15 | 728
Fault9 | 0 | 729 | VerDiffFault | 软件版本不一致 | Software version inconsistency
| 1 | 730 | SCICommFault | SCI通信故障 | SCI communication failure
| 2 | 731
| 3 | 732
| 4 | 733
| 5 | 734
| 6 | 735
| 7 | 736
| 8 | 737
| 9 | 738
| 10 | 739
| 11 | 740
| 12 | 741
| 13 | 742
| 14 | 743
| 15 | 744
Fault10 | 0 | 745 | DCDC CountWarn | DCDC数量错误 | DCDC count error
| 1 | 746 | PCU CountWarn | PCU数量错误 | PCU count error
| 2 | 747 | BMS CountWarn | BMS数量错误 | Wrong number of BMS
| 3 | 748
| 4 | 749
| 5 | 750
| 6 | 751
| 7 | 752
| 8 | 753
| 9 | 754
| 10 | 755
| 11 | 756
| 12 | 757
| 13 | 758
| 14 | 759
| 15 | 760

## Version update log
Change the date | address | 修改说明 | Modification Notes
2020-05-23 | 0x0940 | 增加Bit4 | Adding Bit4
| 0x0404 | 增加2种新状态描述 | Add 2 new status descriptions
| 0x09C0 | 增加Bit3 | Addition of Bit3
| 0x09DB-0x09DE | 新增参数 | Add new parameters
| 0x2006 | 更新值定义描述 | Updated value definition descriptions
2020-06-03 | 0x102D | 新增CT自动校正寄存器 | New CT auto-calibration register
2020-06-10 | 0x0940 | 增加Bit5 | Add Bit5
2020-06-29 | 0x0914-0x0915 | 新增参数 | Add new parameter
| Fault2-byte1-bit6 | 新增故障 | New fault
| Fault3-byte1-bit6 | 新增故障 | New fault
2020-08-31 | 0x1046 | 增加电池协议类型 | Add battery protocol type
| 0x1038 | 新增地址 | Add address
| 0xA07C-0xA07F | 新增地址 | Add address
| Fault3-byte0-bit5 | 增加InverterSoftStartFail | Add InverterSoftStartFail
| Fault3-byte1-bit7 | 增加SNTypeFault | Add SNTypeFault
| Fault9-byte1-bit5 | 增加unrecoverSpdFail(DC) | Add unrecoverSpdFail(DC)
| Fault9-byte1-bit6 | 增加unrecoverSpdFail(AC) | Add unrecoverSpdFail(AC)
| Fault2-byte0-bit1 | 修改故障名称 | Modify fault name
| Fault2-byte1-bit0 | 增加HwADFaultDCI(DC) | Add HwADFaultDCI(DC)
| Fault2-byte1-bit1 | 增加HwADFaultIdcBranch | Add HwADFaultIdcBranch
| Fault10-byte1-bit4 | 修改故障名称 | Modify fault name
| Fault10-byte1-bit5 | 增加BMS2CommunicatonFault | Add BMS2CommunicatonFault
| Fault10-byte1-bit6 | 增加BMS3CommunicatonFault | Add BMS3CommunicatonFault
| Fault10-byte1-bit7 | 增加BMS4CommunicatonFault | Add BMS4CommunicatonFault
| Fault10-byte0-bit7 | 增加SafetyVerFault | Add SafetyVerFault
2020-09-04 | 0x803C-0x803F | 新增地址 | Add new address
| 0x9000-0x9FFF | 新增BMS透传区 | Add BMS Transmissions Zone
| 0x06D1-0x06E2 | 新增地址 | Add Address
| Fault5-byte1-bit1 | 新增FlyingCapOVP | Added FlyingCapOVP
2020-10-13 | 0x08C8-0x08CC | 增加安规参数 | Add safety parameters
| 0x0A04-0x0A05 | 增加安规参数 | Added safety parameters
| 0x1050 | 电压精度问题修复 | Fixed voltage accuracy issue
2020-10-30 | 0x9000-0x9FFF | BMS透传区实时数据部分新增包ID | Package IDs added to the real time data section of the BMS transmission area
| 0x4B0-0x4B9 | 新增地址 | Addresses added
| 0x522-0x527 | 新增地址 | Addresses added
| Fault11-byte1-bit7 | 增加故障 | Fault added
2020-11-16 | 0x1039-0x103D | 新增地址 | Addresses added
2020-12-02 | 0x0901，0x0A03 | 原地址取值范围更新 | Original address range updated
| 0x1046 | 原地址取值范围更新 | Original address range updated
| 0x1052 | 新增电池参数地址 | Battery parameter address added
| 0x1054-0x1056 | 新增电池参数地址 | Battery parameter address added
| 0x1023 | 原地址取值范围更新 | Original address range updated
| 0x1024 | 原地址单位更新 | Original address units updated
| 0x1084-0x108C | 新增拉弧配置地址 | Arc pull configuration address added
| 0xA070-0xA075 | 新增地址 | New address added
| 0x0780-0x07BF | 增加拉弧实时信息区 | Real-time information area added for arc pulling
| 0x2007-0x200B | 新增安规国家名称地址 | New safety country name address added
| 0x0432-0x043A | 增加故障信息地址 | Add fault information address
| Fault6-byte1-bit0 | 增加SwPvOCP | Add SwPvOCP
| Fault26/27 | 新增AFCI故障 | Added AFCI fault
2021-01-27 | 0x9005 | 日期寄存器类型问题修复 | Date register type issue fixed
| 0x9051-0x906A, 0x9079, 0x9091-0x90AA, 0x90B4 | 精度变更 | Accuracy change
| 0x907A | 新增地址 | New address added
| 0x1105-0x110B | 新增地址 | New address added
| 0x04BA-0x04BC | 新增地址 | Address added
| 0x108D-0x108E | 新增地址 | Address added
| Fault11-byte1-bit6 | 新增FanFault7 | Added FanFault7
| Fault12-byte0-bit6 | 新增BMS VerFault | Added BMS VerFault
| Fault12-byte0-bit7 | 新增BMS CAN VerFault | Added BMS CAN VerFault
| Fault12-byte1-bit0 | 新增BMS CAN VerLow | Added BMS CAN VerLow
| Fault12-byte1-bit4 | 新增AFCICommLose | Added AFCICommLose
| Fault12-byte1-bit5 | 新增DCArcingAlarmFault | Added DCArcingAlarmFault
2021-02-05 | Fault7-byte1-bit0 | 新增MeterCommFault | Added MeterCommFault
2021-02-16 | 0x118D-0x1190, 0x1197-0x119A, 0x11A1-0x11A4 | 数据类型更新 | Data type update
| 0x1035 | 更新寄存器取值范围和取值定义 | Updated register value range and value definition
| Fault6-byte1-bit1 | 新增IbalanceOCP | IbalanceOCP added
| 0x1024 | 修复精度问题 | Fixed accuracy issue
2021-03-16 | Fault1-byte1-bit3 | 字段名修正 | Field name fixes
| Fault1-byte1-bit4 | 新增防逆流过载故障 | Added anti-backflow overload fault
| Fault8-byte1-bit3 | 字段名修正 | Field name correction
| 0x460-0x465 | 新增安规版本号寄存器 | Added safety version number register
| 0x0951-0x0960 | 新增安规参数地址 | Added safety parameter address
| 0x0980 | 原地址新增位域定义 | New bit field definition for original address
| 0x0981 | 最大值最小值修正，请查看批注 | Maximum and minimum values corrected, see comments
| 0x0982 | 最大值最小值修正 | Maximum and minimum values corrected
| 0x0993 | 原地址字段、单位、备注更新 | Original address field, units, remarks updated
| 0x0995 | 原地址地段、备注更新 | Original address lot, comments updated
| 0x0996 | 原地址字段、类型、备注更新 | Original address field, type, comments updated
| 0x09A1 | 新增安规参数地址 | Addresses for safety parameters added
| 0x09C0 | 原地址新增位域定义 | Original address bit field definition added
| 0x0A00 | 原地址新增位域定义 | Original address new bit field definition
2021-06-19 | 0x05C4 | 增加PV总功率地址 | Total PV power address added
| 0x0667-0x0669 | 增加电池汇总信息地址 | Add battery summary information address
| 0x0916 | 增加电压降载时间地址 | Add voltage drop time address
| 0x0940 | 增加Bit6 | Add Bit6
| 0x0961-0x0962 | 增加过、欠频功率穿越点频率地址 | Add over and under frequency power crossing point frequency address
| 0x1060 | 增加PCC功率采集设备配置地址 | Add PCC power harvesting device configuration address
| Fault4-byte1-bit5 | 增加故障位 | Add fault bits
2021-08-03 | 0x1098-0x109C | 新增PID配置地址 | Add PID configuration address
| 0x110F | 新增PID控制地址 | Add PID control address
| Fault12-byte1-bit6 | 新增故障 | Add fault
2021-08-11 | 0x044C | 由保留地址变更为有效序列号地址 | Change from reserved address to valid serial number address
| 0x0470-0x0476 | 新增2个有效序列号地址，和5个保留地址 | Added 2 valid serial number addresses, and 5 reserved addresses
| 0x10A0-0x10A1 | 新增PLC使能和配置地址 | Added PLC enable and configuration addresses
| 0x10A5-0x10A6 | 新增BLE使能和配置地址 | New BLE enable and configuration address
| 0x10B0-0x10A4 | 修改PID使能和配置地址 | Modified PID enable and configuration addresses
| 0x8027 | 由保留地址变更为有效序列号地址 | Changed from reserved to valid serial number addresses
| 0x8028-0x802E | 新增2个工厂有效序列号地址，和5个保留地址 | Added 2 factory valid serial number addresses, and 5 reserved addresses
| 0x802F-0x8032 | 新增外设配置地址和外设配置BIT对应表 | New peripheral configuration address and peripheral configuration BIT correspondence table
| 0xA06A | 新增远程复位指令 | New remote reset command
| Fault12-byte1-bit7 | 新增PLC心跳故障 | New PLC heartbeat fault
2021-08-31 | 0x1108 | 地址数据类型变更为有符号 | Address data type changed to signed
| Fault13、Fault14 | 告警名称变更 | Alarm name change
| 0x0040-0x0043 | 增加协议“通用”区 | Protocol "General" area added
| 0x0044 | 增加协议版本号 | Protocol version number added
2021-09-06 | Fault8-byte1-bit0 Fault8-byte1-bit1 | 新增防雷故障(DC)和防雷故障(AC) | Lightning protection fault (DC) and lightning protection fault (AC) added
| 0x0044 | 更新协议版本定义 | Updated protocol version definition
| 0x0045-0x0047 | 增加芯片代号 | Addition of chip code
2021-10-11 | 0x0940 | 增加Bit7定义 | Addition of Bit7 definition
2021-11-03 | 0x1023 | 增加模式定义：相功率模式 | Add mode definition: phase power mode
| 0x1034 | 语言定义 | Language definition
| 0x1061 | 增加谐振检测灵敏度寄存器 | Add resonance detection sensitivity register
| 0x1110 | 增加模式定义：离网模式 | Add mode definition: off-grid mode
| 0x1144-0x1146 | 新增离网模式寄存器 | Add off-grid mode register
| 0x203D-0x203F | 增加目标芯片定义：PCU（Power Control Unit）和BMS（Battery Management System） | Add target chip definition: PCU (Power Control Unit) and BMS (Battery Management System)
| 0x7000-0x707F | 新增ODM数据定制区域 | New ODM data customisation area
| ID91 | 增加谐振保护ID | Add resonance protection ID
| ID106 | 增加序列号机型错误ID | Add serial number model error ID
2021-12-08 | 0x8020 | 地址错位问题修复 | Address misalignment issue fixed
| 0x1051 | 寄存器定义更新 | Register definition update
| 0x1057-0x105A | 增加铅酸电池相关寄存器 | Lead acid battery related registers added
| 0x100C | 寄存器定义更新 | Register definition update
2021-12-27 | Fault1-byte1-bit5 | 增加电压不平衡故障 | Voltage imbalance fault added
| Fault3-byte0-bit6 | 增加电弧保护 | Arc protection added
| Fault3-byte0-bit7 | 增加弱光检测故障 | Low light detection fault added
| Fault6-byte1-bit2 | 变更为谐振保护 | Change to resonance protection
| Fault6-byte1-bit3 | 增加主播限流保护 | Add anchor current limit protection
| Fault7-byte1-bit1 | 增加序列号机型故障 | Add serial number model fault
| Fault12-byte1-bit5 | 删除电弧报警 | Remove arcing alarm
2022-04-24 | PCU故障位说明 | 增加故障说明页 | Add fault description page
| 0x0404 | 增加新状态 | Add new status
| 0x0466-0x046A | 增加AFCI版本 | Add AFCI version
| 0x0510、0x0518、0x0520 | 修改字段为应急负载电压 | Modify field to emergency load voltage
| 0x06E3-0x06EC | 增加内部信息寄存器 | Add internal information register
| 0x0744-0x0763 | 增加组串3、4路电流 | Add group string 3 and 4 way currents
| 0x0784-0x07A1 | 修改拉弧信息字段 | Modify arc pull information field
| 0x1046 | 更新寄存器定义 | Update register definition
| 0x1085-0x1092 | 修改电弧配置字段 | Modify arc configuration field
| 0x1110 | 增加模式定义：发电机模式 | Add mode definition: generator mode
| 0x2039-0x203C | 新增寄存器支持一对多升级和静默下载 | Add register support for one-to-many upgrades and silent downloads
| 0x6000-0x6FFF | 新增PCU数据区 | Added PCU data area
| 0x7000 | 更新定义 | Update definitions
2022-05-30 | 0x8019-0x801A | 生产管理区:0x8019-0x801A表格重复，删掉重复行 | Production management area:0x8019-0x801A table duplicate, delete duplicate rows
| 0x0466-0x046A | 版本更新记录（本页133行）地址0x0477-0x047B订正 | Version update record (line 133 on this page) address 0x0477-0x047B revised
| Fault12:bit0-5 | 描述的告警改为保护 | Description of alarms changed to protection
| 0x8012-0x8013 | 增加读写总发电量 | Add read/write total power generation
| 0x900D | 修改描述：低8位所有电池包电池串数 | Revision of description: low 8 bits all battery pack battery string count
| 0x9010 | 修改类型: U16改为I16 | Revision type: U16 to I16
| 0x9079 | 修改精度，由0.01改为0.1 | Revise accuracy from 0.01 to 0.1
| 0x907B | 增加只读本组电池的电池包总串数 | Add read only the total number of battery pack strings for this group of batteries
| 0x907C | 增加只读本组单个电池包的电池单体串数 | Add read only the number of individual battery strings for this group of cells in a single pack
| 0x90B8 | 增加只读本组电池的电池包总数 | Increase the total number of battery packs for this group of batteries only
| 0x90B9 | 增加只读本组单个电池包的电池单体串数 | Increase the number of individual strings of batteries in this group of individual packs only
| Fault11:bit4-bit6 | 修改故障165-167删除 | Modify Fault 165-167 Delete
2022-06-27 | 0x43B-0x43D | 新增Fault28-Fault29默认不使能位区域 | Added Fault28-Fault29 default disable bit area
| Fault28 | 新增协议版本错误(ARM) | Added protocol version error (ARM)
| Fault29:bit0 | 修改零地电压过高(删除Fault0:bit15) | Modify zero ground voltage too high (delete Fault0:bit15)
| Fault29:bit1 | 修改PV支路软件过流(删除Fault6:bit13) | Modified PV branch software overcurrent (Fault6:bit13 deleted)
| 0x1147 | 新增干接点控制方式设置 | New dry contact control mode setting
| 0x45E-0x45F | 新增BOOT版本号(主DSP，副DSP) | New BOOT version number (primary DSP, secondary DSP)
| 0x2100-0x213F | 新增电力载波通讯PLC参数区 | New PLC parameter area for power carrier communication
| 0x1046 | 新增电池参数-通讯协议 11：动为 | New battery parameters - communication protocol 11: move for
2022-07-27 | 0x6048-0x604E | 新增MODBUS协议新增PCU电压电流校准系数 | New MODBUS protocol New PCU voltage and current calibration coefficient
| 0x11C4-0x11C8 | 新增电站通讯中断保护功能寄存器 | New power station communication interruption protection function register
| Fault11-byte0:bit3 | 新增故障ID164 "PSCommFault" "电站通讯故障关机" | New fault ID 164 "PSCommFault" "Power Station Communication Fault Shutdown"
| 0x200D | 新增:协议设置寄存器 | New:Protocol setting register
| 0x8012-0x8013 | 总发电量修改为只写 | Total power generation modified to write only
| 0x1046 | 新增电池参数-通讯协议11:BTS 5K 修改电池参数-通讯协议 12:动为 | New battery parameters - communication protocol 11:BTS 5K Modify battery parameters-communication protocol 12:move to
| PCU故障位Fault3 | 新增PCU故障位bit6:SwBusInstantOCP:母线软件过流; 新增PCU故障位bit8:PackIDErr:PackID 错误; | New PCU fault bit bit6:SwBusInstantOCP:Bus software overcurrent. New PCU fault bit bit8:PackIDErr:PackID error;
2022-08-31 | 0x0052-0x0054 | 启用预留地址，增加协议版本号的读取(ARM/DSPM/DSPL) | Enable reserved address, add protocol version number reading (ARM/DSPM/DSPL)
| Fault2.byte1.bit7/Fault9.byte1.bit | 新增Fault2.byte1.bit7中性点接地故障； 新增Fault9.byte1.bit电网继电器故障 | New Fault2.byte1.bit7 neutral ground fault; New Fault9.byte1.bit grid relay fault
| 0x066A | 新增电池信息区增加“实时电池路数” | New battery information area with "Real-time battery paths"
| 0x06ED | 新增“逆变器额定功率”，单位0.1kW，只读 | Added "Inverter power rating" in 0.1kW, read only
| 0x60A1-60A2 | 新增“组串总路数/电池总路数”，只读 | Added "Total number of strings / total number of battery circuits", read only
| 0x60C5~60C7 | 新增操作指定路数的编号和对应组串/电池额定功率 | Added the number and the corresponding string/battery power rating for the operation of the specified number of circuits
| 0x200D | 新增0x0005:solarmax协议 | Added 0x0005:solarmax protocol
| 0x1062 | 新增CT变比设置 | New CT ratio setting
| 0x1063 | 新增硬防逆流开关 | New hard anti-backflow switch
| 0x102E | 修改意大利测试S/F的描述 | Modified the description of the Italian test S/F
| Fault7-byte1-bit0 Fault11-byte1-bit7 | 修改故障位域说明，删去电表通讯故障重复 | Modification of the description of the fault bit field, deletion of the meter communication fault repetition
| 0x2100-0x213F | 修改电力载波通讯PLC参数区 | Modified power carrier communication PLC parameter area
2022-10-25 | Fault7-byte0-bit7 | 新增故障位 HwDiffOCP/硬件差分过流 | New fault bit HwDiffOCP/hardware differential overcurrent
| 0x6011-601A | PCU SN码类型ASCII改为U16 | PCU SN code type ASCII changed to U16
| 0xA0C4--0xA0CB | DSPStatus1-8内部调试信息(在内部信息区)重复定义删除 | DSPStatus1-8 internal debug information (in internal information area) duplicate definition deleted
| 0x6000 | 内部信息为LCD显示的调试信息内容，增加提示说明 | Internal message is the content of the debug message displayed on the LCD, add prompt description
| 0x2037-0x2038 | 增加文件类型的升级和进度显示 | Added file type upgrade and progress display
| 0x9018-0x901B | 新增了首航BMS软件版本的读取 | Added reading of Shouhang BMS software version
| 0x1034 | 语言增加14.捷克语 | Language added 14. Czech
| Fault28-byte1-bit0 | 增加设置过压保护事件 | Added setting of over-voltage protection event
| 0x5000-0x5FFF | 新增DCDC数据区（0x5000-0x5FFF）及故障位说明； | Addition of the DCDC data area (0x5000-0x5FFF) and description of the fault bits;
| 0x2034-2036,0x203F | 新增DCDC-ARM/DSP升级标志位 | New DCDC-ARM/DSP upgrade flag bit
| PCU故障位Fault2-bit13/Fault3-bit9 | PCU新增两个故障标志位 | Two new fault flag bits added to PCU
| 0x1064-0x1065 | 干接点控制从0x1147(没有使用）改到0x1064,预留湿接点控制 | Dry contact control changed from 0x1147 (not used) to 0x1064, wet contact control reserved
2022-12-26 | 0x2037 | 文件类型写入BIT改为BYTE值 | File type write BIT changed to BYTE value
| 0x200E-200F | 增加安规文件包的设置 | Added setting for safety file package
| Fault6-byte1-bit4 | ID93:PV支路软件过流（默认使能） | ID93:PV branch software overcurrent (enabled by default)
| 0x203C-203E(bit7),0x203F | AFCI升级，AFCI芯片代码使用新标准，芯片类型改为0x42 | AFCI upgrade, AFCI chip code using new standard, chip type changed to 0x42
| 0x1060 | 新增采集器方式 | New collector method added
| 0x0900 | 增加远程关机降载使能位 | Add remote shutdown down load enable bit
| PCU故障位Fault3 | 增加ID906母线平均值欠压位 | Add ID906 bus average undervoltage bit
| 0x06EE | 增加IV曲线扫描有效点的个数 | Increase the number of valid points for IV curve scanning
| 0x4E20 | 新增VersionType用于启用当前生效的协议版本 | New VersionType for enabling the protocol version currently in effect
| Fault5-byte1-bit3 | 新增PVUVP(PV欠压) | New PVUVP (PV undervoltage)
2023-02-27 | Fault1-byte1-bit6/bit7 | 新增逆变瞬时值过压/电网相变突变 | New Inverter Transient Value Over Voltage / Grid Phase Change Sudden Change
| Fault8-byte0-bit5 | 新增低温降载 | New low temperature load shedding
| Fault12-byte1-bit1/2/3/5 | 增加电池放电/充电，过温/低温保护 | Add battery discharge/charge, overtemperature/low temperature protection
| 0x069C-0x06B3 | 增加当年当月的电量统计数据 | Added power statistics for the current month of the year
| 0x9020/0x9084 | 修改描述：控制字的范围都是从1开始 | Modified description: The range of control words all start from 1
| 0xA07D | 修改描述：韩国DEV-AVM协议测试标志 | Modified description: Korean DEV-AVM protocol test flags
2023-04-17 | 0x9020,0x9084 | 控制字的范围都是从0开始。即0表示第1包数据，也表示第一组电池 | The range of control words all start from 0. i.e. 0 means the 1st pack of data and also the first set of batteries
| 0x2040-0x2048 | EP增加定时升级功能 | EP adds timed upgrade function
| PCU故障位Fault3 | 增加PCU故障位ID907/908 | Add PCU fault bit ID 907/908
| Fault2-byte1-bit2 | 增加027PV-对地阻抗低 | Add 027PV - low impedance to ground
| 0x1066 | 增加PV支路过流保护 | Add PV branch overcurrent protection
| 0x203D | 增加远程升级支持整包 | Add remote upgrade support for whole pack

## Mask
Mask Name | High character | Low words | Mask description: | When mask is 0, write is invalid, read is indeterminate
AddressMask_General1 | 00000000 | 0000000F
AddressMask_Realtime_SysInfo1 | 00000000 | 0000000F
AddressMask_Realtime_SysInfo2 | 00000000 | 0000000F
AddressMask_Realtime_GridOutput1 | 00000000 | 0000000F
AddressMask_Realtime_EmergencyOutput1 | 00000000 | 0000000F
AddressMask_Realtime_Input_PV1 | 00000000 | 0000000F
AddressMask_Realtime_Input_PV2 | 00000000 | 0000000F
AddressMask_Realtime_Input_Bat1 | 00000000 | 0000000F
AddressMask_Realtime_Input_Bat2 | 00000000 | 0000000F
AddressMask_Realtime_ElectricityStatistics1 | 00000000 | 0000000F
AddressMask_Realtime_ClassifiedInfo1 | 00000000 | 0000000F
AddressMask_Realtime_CombinerInfo1 | 00000000 | 0000000F
AddressMask_Realtime_CombinerInfo2 | 00000000 | 0000000F
AddressMask_Config_Basic1 | 00000000 | 0000000F
AddressMask_Config_Basic2 | 00000000 | 0000000F
AddressMask_Config_Basic3 | 00000000 | 0000000F
AddressMask_Config_Remote1 | 00000000 | 0000000F
AddressMask_Config_Remote2 | 00000000 | 0000000F
AddressMask_Config_Remote3 | 00000000 | 0000000F
AddressMask_Config_Remote4 | 00000000 | 0000000F
AddressMask_Config_ReadOnly_Result1 | 00000000 | 0000000F
AddressMask_Config_ReadOnly_Result2 | 00000000 | 0000000F
AddressMask_Config_ReadOnly_Result3 | 00000000 | 0000000F
AddressMask_Config_ReadOnly_Result4 | 00000000 | 0000000F
AddressMask_Config_ReadOnly_Result5 | 00000000 | 0000000F
AddressMask_Config_ReadOnly_Result6 | 00000000 | 0000000F
AddressMask_Config_Core1 | 00000000 | 0000000F
AddressMask_Factory1 | 0000007F | 0003FFFF
AddressMask_Factory2 | 00000000 | 0000000F
AddressMask_Factory3 | 00000000 | 0000000F
AddressMask_BMS1_System | 00000000 | 0000000F
AddressMask_BMS2_Realtime | 00000000 | 0000000F
AddressMask_BMS3_Fault | 00000000 | 0000000F
AddressMask_Admin1 | 00000000 | 0000000F
AddressMask_Admin2 | 00000000 | 0000000F
AddressMask_Admin3 | 00000000 | 0000000F

## Measured messages
Example 1：
Power-on parameter screen (0X0800-0X083F) Actual telegram write data: 01 10 08 00 00 40 80 00 30 00 64 00 3C 00 09 15 5F 10 F3 13 92 12 8E 15 5F 10 F3 13 92 12 8E FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF E8 A6 Write answer: 01 10 08 00 00 40 C3 99 The write command is parsed as follows: 01 10 means the device address is 01 and function code 10 is written to the function 08 00 indicates the start address of the interface register 00 40 means that 64 registers are written (in hex) 80 means that a total of 128 bytes of data are written 00 30 means 08 00 address register written for a value of 48 seconds 00 64 means that the 08 01 address register is written at a value of 100 rise rate 00 3C means that the 08 02 address register has a parallel wait time of 60s The following data parsing are analogous, a register accounts for two bytes of storage space, data parsing are hexadecimal, undefined registers are all written 1, that is, all set to FF FF, the last two bytes E8 A6 for CRC check code. Write-to-answer parsing: 01 10 means set address is 01, function code is 10 08 00 means the start address of the interface register 00 40 means that 64 registers are written C3 99 means CRC check digit
Example 2：
Power-on parameter interface (0X0800-0X083F) actual test message Reading data: 01 03 08 00 00 40 46 5A Read the answer： 01 03 80 00 30 00 64 00 3C 00 09 15 5F 10 F3 13 92 12 8E 15 5F 10 F3 13 92 12 8E FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF 75 E8 Explanation of read command: 01 03 indicates the device address 01 and function code 03 read function 08 00 indicates the start address of the read interface register 00 40 indicates the number of registers to be read 46 5A indicates CRC check digit Read answer parsing: 01 03 indicates device address and function code. 80 means 128 bytes read 00 30 means 08 00 address register read 00 64 means 08 01 address register read data 00 3C means 08 02 address register read data In turn, two bytes correspond to one register analogously, the full value of the undefined register is FF FF corresponding to the write, 75 E8 is the CRC check code. Waiting time before grid connection (0X0800) is set to 60s Actual message write sent: 01 10 08 00 00 01 02 00 3C 2F 81 Answer 1: 01 10 08 00 00 01 03 A9 Read transmission of the actual message: 01 03 08 00 00 01 86 6A Answer 2: 01 03 02 00 3C B8 55 Note: The single function registers in this interface can all be written and read, similar to the waiting time before grid connection, by setting the address to correspond to the data range.
Example 3：
Crypto, GFCI, ISO parameter interface (0x0A00-0x0A3F) Write command: 01 10 0A 00 00 40 80 00 01 00 01 00 03 00 14 00 32 00 00 FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF F7 8E Write answer: 01 10 0A 00 00 40 C2 21 Write command according to the analysis: 01 10 means the device address is 01, function code 10 write function 0A 00 indicates the start address of the interface register 00 40 means that 64 registers (in hex) are written 80 means that a total of 128 bytes of data are written 00 01 means that the 0A 00 address register is written with a value of 1 (0000 0001), opening the orphan enable register, the low byte binary case corresponds to the enable bit. 00 01 indicates that the 0A 01 address register is written with a value of 1, opening the GFCI enable. 00 03 means that the 0A 02 address register is written to a value of 3, which turns on the insulation impedance enable and the ground detection enable. The following data parsing are analogous, a register accounts for two bytes of storage space, data parsing are hexadecimal, undefined registers are all written 1, that is, all set to FF FF, the last two bytes F7 8E for CRC check code. Write-to-answer parsing: 01 10 means set address is 01, function code is 10 0A 00 indicates the start address of the interface register 00 40 means that 64 registers are written C2 21 means CRC check digit
Example 4：
Crypto, GFCI, ISO parameter interface (0x0A00-0x0A3F) Read commands: 01 03 0A 00 00 40 47 E2 read answer： 01 03 80 00 01 00 01 00 03 00 14 00 32 00 00 FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF 4F A0 This interface register can also be read or written for a single register function, and the operation process is similar to that of Read instruction parsing: 01 03 indicates the device address 01 and function code 03 read function 0A 00 indicates the start address of the read interface register 00 40 indicates the number of registers to be read 47 E2 indicates the CRC check digit Read Answer Explanation: 01 03 indicates device address and function code, 80 indicates 128 bytes read 00 01 indicates 0A 00 address register read data 00 01 means 0A 01 address register read data 00 03 means 0A 02 address register read data In turn, two bytes correspond to a register analogy, the full value of the undefined register is FF FF and write correspondence, 4F A0 is CRC check code. Set the insulation impedance protection value to 50K. Write instruction: 01 10 0A 03 00 01 02 00 32 8D B6 Answer: 01 10 0A 03 00 01 F2 11 Read command: 01 03 0A 03 00 01 77 D2 Answer: 01 03 02 00 32 39 91
Example 5:
1. Read: // Multi-register reads: 0x40 (64) register values are read from address 0x1000. // Reads of arbitrary length and address are supported within the block address (0x1000 to 0x0103F)发：01 03 10 00 00 40 40 FA receive：01 03 80 41 FF 63 FE 00 1E FF FF 00 16 00 0C 00 07 00 0A 00 2B 00 25 00 00 00 01 00 01 00 00 00 00 00 00 00 00 00 80 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 01 00 00 00 01 00 05 00 00 00 00 00 00 00 02 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 01 00 00 00 01 00 00 00 00 00 00 00 00 00 00 00 00 00 00 B0 3E Receiving Analysis：80：A total of 0x80 bytes of data was read。 41 FF: Data at address 0x1000. Represents validity of addresses 0x1030 to 0x103F 63 FE: Data at address 0x1001. Represents validity of addresses 0x1020 to 0x102F 00 1E: Data for address 0x1002. Valid for representing addresses 0x1010 to 0x101F FF FF: Data for address 0x1003. Represents validity of addresses 0x1000 to 0x100F 00 16: Data for address 0x1004. 22 years 00 0C: Data for address 0x1005. 12 months 00 07: Data for address 0x1006. 7 days 00 0A: Data for address 0x1007. 10 points 00 2B: Data for address 0x1008. 43 pts 00 25: Data for address 0x1009. 37 sec. 00 00: Data for address 0x100A. 00 00: Data for address 0x100A. Last write time operation successful 00 01: Data at address 0x100B. RS485 address is 1 00 01: Data at address 0x100C. Bit rate is 9600 00 00: Data at address 0x100D. Stop bit is 1 00 00: Data for address 0x100E. No parity bit 00 00: Data at address 0x100F. Last write to RS485 configuration successful 00 00: Data at address 0x1010. PV input mode is parallel 00 80: Data at address 0x1011. Input channel 0 is battery input 00 00: Data at address 0x1012. Input channel 1 is not used 00 00: Data at address 0x1013. Input channel 2 is no tused 00 00: Data at address 0x1020. Input channel 15 is not used 00 00: Data at address 0x1021. Last operation on input channel successful 00 00: Data at address 0x1022. Last reading of safety parameters from USB stick successful 00 01: Data at address 0x1023. Anti-backflow set to default mode 00 00: Data at address 0x1024. Anti-backflow power set to 0 00 01: Data at address 0x1025. IV scan enabled 00 05: Data for address 0x1026. IV scan period is 5 minutes 00 00: Data at address 0x1027. Last operation IV scan successful 00 00: Data at address 0x1028. IV curve value passed to PV0 00 00: Data at address 0x1029. Turn off emergency power enable 00 02: Data at address 0x102A. Emergency power supply start wait 2s 00 00: Data at address 0x102B. Disable automatic battery activation 00 00: Data at address 0x102C. Last automatic battery activation command successful 00 00: Data at address 0x102D. Last CT auto-calibration operation successful 00 00: Data at address 0x102E. Last Italian automatic test operation successful 00 00: Data at address 0x102F. Blank 00 00: Data at address 0x1030. Electricity statistics for the first 0 years of the current year score 00 00: Data at address 0x1031. Power statistics for the first 0 months of the current month division 00 00: Data at address 0x1032. Power statistics for the previous 0 days of the current day 00 00: Data for address 0x1033. Invalid data 00 00: Data for address 0x1034. Inverter language is Chinese 00 00: Data for address 0x1035. Disable parallel function 00 01: Data at address 0x1036. Local machine set to host 00 00: Data at address 0x1037. Local parallel address is 0 00 01: Data at address 0x1038. Enable unbalance support 00 00: Data for address 0x1039. Generating power multiplier of 0 00 00: Data for address 0x103A. Buy power multiplier is 0 00 00: Data at address 0x103B. Sell power multiplier is 0 00 00: Data for address 0x103C. Charge power multiplier of 0 00 00: Data at address 0x103D. Discharge quantity multiplier is 0 00 00: Data at address 0x103E. Logic interface control disabled 00 00: Data at address 0x103F. Blank // Single register read: supports any read within addresses 0x1000 to 0x103F Send: 01 03 10 04 00 01 C1 0B Receive: 01 03 02 00 16 39 8A Receive resolution: 0x0016 for address 0x1004, current year is 2000 + 0x0016 = 2022